## Main Compliance Page
Quick Links | Compliance Worksheet Instructions |  |  |  | ASHRAE/IES 90.1-2010 Lighting Compliance Documentation (v3.1) | [6 empty] | Select Version > | 2010 | 2010 | 2 | _2010_Space_by_SpaceTypes | 90.1-2010
| Throughout this form Fill in all YELLOW cells |  |  |  | Project Name:
| Mouse over this |  |  |  | Address:
| red triangle | for more info |  |  | City/Sate/ZIP:
| Click on blue text to go to each step/section |  |  |  |  | Name |  | Email Address |  |  | Telephone
[5 empty] | Designer: | [12 empty] | www.ashrae.org
|  |  | 90.1-2010 |  | Project Contact: | [12 empty] | www.ies.org
COMPLIANCE
[5 empty] | Pre Installation Compliance: |  |  |  |  | Post Installation Compliance:
[5 empty] | Interior | TBD | [5 empty] | No
[5 empty] | Exterior | TBD | [5 empty] | Yes
ALTERATIONS
Is this lighting installation an alteration to an existing system (Yes/No)?:
No
[5 empty] | Claiming 9.1.2 exception (Yes/No)? | No
9.1.2 exception Interior Alterations
[5 empty] | 9.1.2 exception Exterior Alterations | Compliant
LIGHTING POWER
|  |  |  | Select Compliance Method? |  | 9.3 Interior Lighting Power: | [5 empty] | Exterior Lighting Power:
[6 empty] | TBD |  |  |  |  | TBD
Space by Space Not Used
[7 empty] | 9.4 Mandatory Requirements: |  |  |  |  | 9.4 Mandatory Requirements:
[5 empty] | Interior Controls: | TBD |  |  |  | Exterior Controls: | TBD
|  |  | WATTS ALLOWED |  |  | 1
[5 empty] | 9.5 Building Area Method | 1 |  |  |  |  | Exterior Lighting Power Allowance (ELPA):
[6 empty] | 0 |  |  | Total Exterior Power Allowance: |  |  | 0
[6 empty] | 0 | [5 empty] | Not Selected
0
[5 empty] | 9.6 Space-by-Space Method | 1 | [5 empty] | 0
[8 empty] | 1 | 1
|  |  | Total Interior Lighting Power Allowance (ILPA): |  |  | Not Used
Not Used
Not Used
Not Used
Not Used
WATTS INSTALLED
[5 empty] | Total Installed Interior Lighting Power | 0 |  |  |  |  | Total Installed Exterior Lighting Power: | 0
[6 empty] | 0 | [5 empty] | 0 |  | #VALUE! | Installed Tradable wattage exceeds allowance + base allowance
[6 empty] | 0 | [5 empty] | 0 |  | 1 | Installed NonTradable wattage exceeds allowance + base allowance
[6 empty] | 0 | [7 empty] | #VALUE!
ASHRAE/IES 90.1-2010 Lighting Compliance Documentation
| ASHRAE/IES 90.1-2016 Lighting Compliance Documentation | [15 empty] | #REF!
#REF!
#REF!
Other Useful Information
9.1.1 Scope
9.1.2 Lighting Alterations
9.1.3 Installed Lighting Power
9.1.4 Interior and Exterior Luminaire Wattage
9.2 Compliance Path(s)
9.6.3 Room Geometry Adjustment
1
Note on A12: Click to go to the top of page
Note on A16: Click link to go to the Project information section (Name, Address and Contact information)
Note on A18: Click the link to select if the project is a building Alteration or New Construction
Note on A20: Click the link to go to the selection of Building Method Method or Space by Space Method for the interior lighting of this project
Note on A22: Click on this link to go to the Interior Room Schedule to enter the spaces on this project.
Note on A24: Click on this link to go to the Interior Room Schedule to enter the spaces on this project.
Note on A26: Click on this link to go to the Luminaire Schedule and enter the lights used on this project.
Note on A28: Click this link to go to the installed Interior Lighting page when using the Building Area Method and enter all of the planned lighting.
Note on A32: Click this link to go to the installed Interior Lighting page when using the Space by Space Method and enter all of the planned lighting.
Note on A36: Click this link to go to the installed Exterior Lighting page and enter all of the planned lighting.
Note on B7: Throughout this Workbook you will see these RED triangles. Move your mouse over the cell to find additional instructions or information on the cells below.
Note on H24: 9.1.2 Lighting Alterations. The alteration of lighting systems in any building space or exterior area shall comply with the lighting power density (LPD) requirements of Section 9 applicable to that space or area and the automatic shutoff requirements of 9.4.1.1. Such alterations shall include all luminaires that are added, replaced or removed. This requirement shall also be met for alterations that involve only the replacement of lamps plus ballasts. Alterations do not include routine maintenance or repair situations. Exception: Alterations that involve less than 10% of the connected lighting load in a space or area need not comply with these requirements provided that such alterations do not increase the installed LPD.
Top of Page
Base ELPA:
Tradable ELPA:
NonTradable Exterior Power:
Total Interior Lighting Power Allowance:
Installed General Lighting:
Installed Decorative Lighting:
Installed Rettail Display Lighting:
Base ILPA:
Decorative ILPA:
Retail Display ILPA:
1 - Project Information
3 - Choose Interior Compliance Method
4 - Fill in Interior Room Schedule
6 - Fill in the Luminaire Schedule
Total Installed Interior Lighting Power:
7 - Building Area Method
Installed Interior Lighting
Tradable Exterior Power:
Control Factors ILPA:
Link to 9.1.2 Alterations Requirements
2 - Alteration (yes/no)
Has 9.4.4 Functional Testing been completed?
Have 9.7 Submittals Requirements been met?
5 - Fill in Exterior Room Schedule
8 - Space by Space Method
Installed Interior Lighting
9 - Installed Exterior Lighting
NonTradable ELPA:
Building Area Method
Space-bySpace Method

## Interior Room Schedule
|  | Quick Links | ASHRAE/IES 90.1-2010 Lighting Compliance Documentation (v3.1)
9.5 Building Area and 9.6 Space by Space Room Schedule
|  |  | Use the table below to enter the 9.5.1 Building Area Method "Building Type(s)" and square footage of each area |  |  |  |  | Use the table below to enter the 9.6.1 Space by Space Method "Space Type(s)" and square footage of each space
[11 empty] | Total Building Sq.ft. |  |  | Base Allowance
|  |  | 2010 | Building Area Method |  |  |  | 2010 | Space By Space Method
[5 empty] | 0 |  | 0 |  |  |  | 0 |  |  | 0
90.1-2010 |  |  | Area ID | 9.5.1 Building Area Method "Building Type" | Enter Building Area (sq.ft) | W/sf.ft. Allowance | Watts Allowed | Space ID | 9.6.1 Space by Space Method "Space Type" | Optional Space Name | Enter Space Area (sq.ft) | Atrium Height (ft) | W/sf.ft. Allowance | Base LPA | #VALUE! | 0
|  |  | 1 |  |  |  | 0 | 1 | [6 empty] | #VALUE!
Room Schedule Instructions |  |  | 2 |  |  |  | 0 | 2 | [6 empty] | #VALUE!
Throughout this form |  |  | 3 |  |  |  | 0 | 3 | [6 empty] | #VALUE!
Fill in all yellow cells |  |  | 4 |  |  |  | 0 | 4 | [6 empty] | #VALUE!
White cells are calculated |  |  | 5 |  |  |  | 0 | 5 | [6 empty] | #VALUE!
|  |  | 6 |  |  |  | 0 | 6 | [6 empty] | #VALUE!
Mouse over this |  |  | 7 |  |  |  | 0 | 7
red triangle | for more info |  | 8 |  |  |  | 0 | 8
|  |  | 9 |  |  |  | 0 | 9
|  |  | 10 |  |  |  | 0 | 10
If you are using the Building Area Method to comply with the Interior Power Allowance, select from the drop down your 9.5 Building Area type(s). Also fill in the square footage of each Building Area. |  |  | 11 |  |  |  | 0 | 11
|  |  | 12 |  |  |  | 0 | 12
|  |  | 13 |  |  |  | 0 | 13
|  |  | 14 |  |  |  | 0 | 14
|  |  | 15 |  |  |  | 0 | 15
|  |  | 16 |  |  |  | 0 | 16
|  |  | 17 |  |  |  | 0 | 17
|  |  | 18 |  |  |  | 0 | 18
If you are using the Space by Space Method to comply with the Interior Power Allowance, select from the drop down your 9.6.1 Space type(s). Also fill in the square footage of each Building Area. |  |  | 19 |  |  |  | 0 | 19
|  |  | 20 |  |  |  | 0 | 20
[5 empty] | Total Building Sq.ft. |  | Total Watts Allowed | 21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
36
37
38
39
40
41
42
43
44
45
46
47
48
49
50
Note on B16: Throughout this Workbook you will see these RED triangles. Move your mouse over the cell to find additional instructions or information on the cells below.
Note on H8: 'Select the 9.5.1 Building Area Method "Building Type" from the Drop Down list. Reference 90.1 Table 9.5.1.
Note on J8: Enter the square footage of each space in the cells below.
Note on O8: 'Select the 9.6.1 Space by Space Method "Space Type(s)" from the Drop Down list. Reference 90.1 Table 9.6.1.
Note on P8: Enter an optional room name. Eg: Classroom 102
Note on Q8: Enter the square footage of each space in the cells below.
Note on R8: Enter the Artium height in feet
Top of Page
Building Area Method Installed Lighting
Create "Building Area Method" Interior Areas
Compliance Main Page
Create "Space by Space Method" Interior Spaces
Space by Space Method Installed Lighting
Link to "Building Area Method" Installed Lighting
Link to "Space by Space Method" Installed Lighting
Exterior Area Schedule
Return to Compliance Workbook

## Exterior Area Schedule
|  | Quick Links | ASHRAE/IES 90.1-2010 Lighting Compliance Documentation (v3.1) | [5 empty] | LZ0 - Undeveloped areas within national parks, state parks, forest land, rural areas, and other undeveloped areas as defined by the authority having jurisdiction
|  |  | Room Schedule | [5 empty] | LZ1 - Developed areas of national parks, state parks, forest land, and rural areas
LZ2 - Areas predominantly consisting of residential zoning, neighborhood business districts, light industrial with limited nighttime use and residential mixed use areas
[5 empty] | Select Appropriate Lighting Zone: |  |  |  | LZ3 - All other areas
[5 empty] | Base Allowance: | Not Selected |  |  | LZ4 - High-activity commercial districts in major metropolitan areas as designated by the local jurisdiction | [8 empty] | #VALUE!
|  |  | 2010 | Tradable Exterior Areas |  |  |  | 2010 | NonTradable Exterior Areas
90.1-2010 |  |  | Space ID | Enter your Exterior Area Name | Select a Building Area Type from the Drop Down list | Enter Area (sq.ft.) | Watts Allowed | Space ID | Enter your Exterior Area Name | Select Building/Area Type from the Drop Down list | Enter Space Area or length | Watts Allowed |  | 0 | 0 |  | 0 |  | 0 |  | 0
|  |  | 1 |  |  |  |  | 1 |  |  |  |  | 1 |  |  | 52 |  |  |  | 1
Room Schedule Instructions |  |  | 2 |  |  |  |  | 2 |  |  |  |  | 2 |  |  | 53 |  |  |  | 2
Throughout this form |  |  | 3 |  |  |  |  | 3 |  |  |  |  | 3 |  |  | 54 |  |  |  | 3
Fill in all yellow cells |  |  | 4 |  |  |  |  | 4 |  |  |  |  | 4 |  |  | 55 |  |  |  | 4
White cells are calculated |  |  | 5 |  |  |  |  | 5 |  |  |  |  | 5 |  |  | 56 |  |  |  | 5
|  |  | 6 |  |  |  |  | 6 |  |  |  |  | 6 |  |  | 57 |  |  |  | 6
Mouse over this |  |  | 7 |  |  |  |  | 7 |  |  |  |  | 7 |  |  | 58 |  |  |  | 7
red triangle | for more info |  | 8 |  |  |  |  | 8 |  |  |  |  | 8 |  |  | 59 |  |  |  | 8
|  |  | 9 |  |  |  |  | 9 |  |  |  |  | 9 |  |  | 60 |  |  |  | 9
|  |  | 10 |  |  |  |  | 10 |  |  |  |  | 10 |  |  | 61 |  |  |  | 10
|  |  | 11 |  |  |  |  | 11 |  |  |  |  | 11 |  |  | 62 |  |  |  | 11
Go to the Tradable Exterior Areas table and enter a area name in the first column. Select a Building Area from the drop down in the second column. Enter the square footage of the exterior area. |  |  | 12 |  |  |  |  | 12 |  |  |  |  | 12 |  |  | 63 |  |  |  | 12
|  |  | 13 |  |  |  |  | 13 |  |  |  |  | 13 |  |  | 64 |  |  |  | 13
|  |  | 14 |  |  |  |  | 14 |  |  |  |  | 14 |  |  | 65 |  |  |  | 14
|  |  | 15 |  |  |  |  | 15 |  |  |  |  | 15 |  |  | 66 |  |  |  | 15
|  |  | 16 |  |  |  |  | 16 |  |  |  |  | 16 |  |  | 67 |  |  |  | 16
Go to the NonTradable Exterior Areas table and enter a area name in the first column. Select a Building Area from the drop down in the second column. Enter the square footage of the exterior area. |  |  | 17 |  |  |  |  | 17 |  |  |  |  | 17 |  |  | 68 |  |  |  | 17
|  |  | 18 |  |  |  |  | 18 |  |  |  |  | 18 |  |  | 69 |  |  |  | 18
|  |  | 19 |  |  |  |  | 19 |  |  |  |  | 19 |  |  | 70 |  |  |  | 19
|  |  | 20 |  |  |  |  | 20 |  |  |  |  | 20 |  |  | 71 |  |  |  | 20
|  |  | 21 |  |  |  |  | 21 |  |  |  |  | 21 |  |  | 72 |  |  |  | 21
|  |  | 22 |  |  |  |  | 22 |  |  |  |  | 22 |  |  | 73 |  |  |  | 22
|  |  | 23 |  |  |  |  | 23 |  |  |  |  | 23 |  |  | 74 |  |  |  | 23
|  |  | 24 |  |  |  |  | 24 |  |  |  |  | 24 |  |  | 75 |  |  |  | 24
|  |  | 25 |  |  |  |  | 25 |  |  |  |  | 25 |  |  | 76 |  |  |  | 25
|  |  | 26 |  |  |  |  | 26 |  |  |  |  | 26 |  |  | 77 |  |  |  | 26
|  |  | 27 |  |  |  |  | 27 |  |  |  |  | 27 |  |  | 78 |  |  |  | 27
|  |  | 28 |  |  |  |  | 28 |  |  |  |  | 28 |  |  | 79 |  |  |  | 28
|  |  | 29 |  |  |  |  | 29 |  |  |  |  | 29 |  |  | 80 |  |  |  | 29
|  |  | 30 |  |  |  |  | 30 |  |  |  |  | 30 |  |  | 81 |  |  |  | 30
|  |  | 31 |  |  |  |  | 31 |  |  |  |  | 31 |  |  | 82 |  |  |  | 31
|  |  | 32 |  |  |  |  | 32 |  |  |  |  | 32 |  |  | 83 |  |  |  | 32
|  |  | 33 |  |  |  |  | 33 |  |  |  |  | 33 |  |  | 84 |  |  |  | 33
|  |  | 34 |  |  |  |  | 34 |  |  |  |  | 34 |  |  | 85 |  |  |  | 34
|  |  | 35 |  |  |  |  | 35 |  |  |  |  | 35 |  |  | 86 |  |  |  | 35
|  |  | 36 |  |  |  |  | 36 |  |  |  |  | 36 |  |  | 87 |  |  |  | 36
|  |  | 37 |  |  |  |  | 37 |  |  |  |  | 37 |  |  | 88 |  |  |  | 37
|  |  | 38 |  |  |  |  | 38 |  |  |  |  | 38 |  |  | 89 |  |  |  | 38
|  |  | 39 |  |  |  |  | 39 |  |  |  |  | 39 |  |  | 90 |  |  |  | 39
|  |  | 40 |  |  |  |  | 40 |  |  |  |  | 40 |  |  | 91 |  |  |  | 40
|  |  | 41 |  |  |  |  | 41 |  |  |  |  | 41 |  |  | 92 |  |  |  | 41
|  |  | 42 |  |  |  |  | 42 |  |  |  |  | 42 |  |  | 93 |  |  |  | 42
|  |  | 43 |  |  |  |  | 43 |  |  |  |  | 43 |  |  | 94 |  |  |  | 43
|  |  | 44 |  |  |  |  | 44 |  |  |  |  | 44 |  |  | 95 |  |  |  | 44
|  |  | 45 |  |  |  |  | 45 |  |  |  |  | 45 |  |  | 96 |  |  |  | 45
|  |  | 46 |  |  |  |  | 46 |  |  |  |  | 46 |  |  | 97 |  |  |  | 46
|  |  | 47 |  |  |  |  | 47 |  |  |  |  | 47 |  |  | 98 |  |  |  | 47
|  |  | 48 |  |  |  |  | 48 |  |  |  |  | 48 |  |  | 99 |  |  |  | 48
|  |  | 49 |  |  |  |  | 49 |  |  |  |  | 49 |  |  | 100 |  |  |  | 49
|  |  | 50 |  |  |  |  | 50 |  |  |  |  | 50 |  |  | 101 |  |  |  | 50
[7 empty] | 0 |  |  |  |  | 0 | 51 | [6 empty] | 51
[13 empty] | 52 | [6 empty] | 52
[13 empty] | 53 | [6 empty] | 53
[13 empty] | 54 | [6 empty] | 54
[13 empty] | 55 | [6 empty] | 55
[13 empty] | 56 | [6 empty] | 56
[13 empty] | 57 | [6 empty] | 57
[13 empty] | 58 | [6 empty] | 58
[13 empty] | 59 | [6 empty] | 59
[13 empty] | 60 | [6 empty] | 60
[13 empty] | 61 | [6 empty] | 61
[13 empty] | 62 | [6 empty] | 62
[13 empty] | 63 | [6 empty] | 63
[13 empty] | 64 | [6 empty] | 64
[13 empty] | 65 | [6 empty] | 65
[13 empty] | 66 | [6 empty] | 66
[13 empty] | 67 | [6 empty] | 67
[13 empty] | 68 | [6 empty] | 68
[13 empty] | 69 | [6 empty] | 69
[13 empty] | 70 | [6 empty] | 70
[13 empty] | 71 | [6 empty] | 71
[13 empty] | 72 | [6 empty] | 72
[13 empty] | 73 | [6 empty] | 73
[13 empty] | 74 | [6 empty] | 74
[13 empty] | 75 | [6 empty] | 75
[13 empty] | 76 | [6 empty] | 76
[13 empty] | 77 | [6 empty] | 77
[13 empty] | 78 | [6 empty] | 78
[13 empty] | 79 | [6 empty] | 79
[13 empty] | 80 | [6 empty] | 80
[13 empty] | 81 | [6 empty] | 81
[13 empty] | 82 | [6 empty] | 82
[13 empty] | 83 | [6 empty] | 83
[13 empty] | 84 | [6 empty] | 84
[13 empty] | 85 | [6 empty] | 85
[13 empty] | 86 | [6 empty] | 86
[13 empty] | 87 | [6 empty] | 87
[13 empty] | 88 | [6 empty] | 88
[13 empty] | 89 | [6 empty] | 89
[13 empty] | 90 | [6 empty] | 90
[13 empty] | 91 | [6 empty] | 91
[13 empty] | 92 | [6 empty] | 92
[13 empty] | 93 | [6 empty] | 93
[13 empty] | 94 | [6 empty] | 94
[13 empty] | 95 | [6 empty] | 95
[13 empty] | 96 | [6 empty] | 96
[13 empty] | 97 | [6 empty] | 97
[13 empty] | 98 | [6 empty] | 98
[13 empty] | 99 | [6 empty] | 99
[13 empty] | 100 | [6 empty] | 100
101
Note on B16: Throughout this Workbook you will see these RED triangles. Move your mouse over the cell to find additional instructions or information on the cells below.
Note on H8: Enter your Exterior Area name
Note on I8: Select the Building Space Type for the drop down list. Building/Space Type (C = Common Space Types) (S = Building Specific Space Types)
Note on J8: Enter the square footage of each space in the cells below.
Note on N8: Enter your Exterior Area name
Note on O8: Select the Building Space Type for the drop down list. Building/Space Type (C = Common Space Types) (S = Building Specific Space Types)
Note on P8: Enter the square footage, Linear footage or Number of areas in the cells below.
Create Tradable Exterior Areas
Create NonTradable Exterior Areas
Return to Compliance Workbook
Top of Page
Compliance Main Page
Tradable Exterior Areas
NonTradable Exterior Areas
Interior Room Schedule

## Luminaire Schedule
|  | Quick Links | ASHRAE/IES 90.1-2010 Lighting Compliance Documentation (v3.1) | [7 empty] | 30 |  |  | 0.8
Luminaire Schedule
[7 empty] | Non Compliant |  |  | Line Voltage Track systems (fill in all yellow cells below for Line Voltage Track) | [7 empty] | OR | Low Voltage Track (fill in yellow cells below. Do NOT fill in any of the Line Voltage numbers!)
£ 5 watts/face?
[10 empty] | specified luminaires and track length |  |  | system’s circuit breaker |  | Optional current-limiting device(s)
90.1-2010 |  |  | Type ID | Description (select from drop down list or enter your own) | Source | If using track lighting select from the dropdown list | Watts per Luminaire (calculate track at right) | Total System Wattage | Track Type Calculated | TOTAL Installed Watts | TOTAL Track Length | Watts at 30W/ft minimum | System Volts | TOTAL Breaker(s) Amps | Current Limiter installed? | System Volts | TOTAL Limiter(s) Amps |  | TOTAL Transformer(s) Wattage |  |  | Installed Wattage | 30W/ft | Line Voltage Max | Circuit | current | Low Voltage |  | 0
[15 empty] | No |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
Luminaire Schedule Instructions | [14 empty] | No |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
Throughout this form | [14 empty] | No |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
Fill in all yellow cells | [14 empty] | No |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #VALUE! | #VALUE! | #VALUE! |  |  |  | 0 | 0 | 0 | 0
White cells are calculated | [14 empty] | No |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [5 empty] | 0 | 0
[15 empty] | No |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [5 empty] | 0 | 0
Mouse over this | [14 empty] | No |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [5 empty] | 0 | 0
red triangle | for more info | [13 empty] | No |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | [5 empty] | 0
[15 empty] | No |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[15 empty] | No |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
Step 1: | [14 empty] | No |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
| The first step is to verify that all Exit Signs meet the < 5 watts per face requirement. Click on the hyperlink above to go directly to the Exit Sign checkoff. | [13 empty] | No |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[15 empty] | No |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[15 empty] | No |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[15 empty] | No |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[15 empty] | No |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | Fixture Types
Step 2: | [14 empty] | No |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | Troffer (1x4)
| The second step is to create your Luminaire Schedule. Click on the hyperlink above to go directly to the Luminaire Schedule. Once there fill in all YELLOW cells. | [13 empty] | No |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | Troffer (2x2)
[15 empty] | No |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | Troffer (2x4)
[15 empty] | No |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | High Bay
[15 empty] | No |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | Low Bay
[15 empty] | No |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | Downlight (lensed)
Step 3: | [14 empty] | No |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | Downlight (open)
| The third step is to return to the Compliance Workbook and enter the lighting to be installed in your building. | [13 empty] | No |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | Downlight (wall washer)
[15 empty] | No |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | Pendant (direct / indirect)
[15 empty] | No |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | Pendant (direct)
[15 empty] | No |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | Pendant (indirect)
[15 empty] | No |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | Linear Industrial
[15 empty] | No |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | Strip
[15 empty] | No |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | Track
[15 empty] | No |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | Wall Sconce
[15 empty] | No |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | Chandelier
[15 empty] | No |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | Cove
[15 empty] | No |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | Task
[15 empty] | No |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | Parking Shoebox
[15 empty] | No |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | Façade Uplight
[15 empty] | No |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | Landscape
[15 empty] | No |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | Wall Pack
[15 empty] | No |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[15 empty] | No |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | Track Types
[15 empty] | No |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | Line Voltage (30W/lf) | 1 | < Enter Calculated Wattage
[15 empty] | No |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | Line Voltage (circuit breaker) | 2 | < Enter Calculated Wattage
[15 empty] | No |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | Line Voltage (current limiter) | 3 | < Enter Calculated Wattage
[15 empty] | No |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #VALUE! | #VALUE! | #VALUE! | Low Voltage (transformer wattage) | 4 | < Enter Calculated Wattage
[15 empty] | No |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[15 empty] | No |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[15 empty] | No |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[15 empty] | No |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[15 empty] | No |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[15 empty] | No |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[15 empty] | No |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[15 empty] | No |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[15 empty] | No |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[15 empty] | No |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[15 empty] | No |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[15 empty] | No |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[15 empty] | No |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[15 empty] | No |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
[15 empty] | No |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #VALUE! | #VALUE! | #VALUE!
Note on B15: Throughout this Workbook you will see these RED triangles. Move your mouse over the cell to find additional instructions or information on the cells below.
Note on H7: Enter a unique luminaire name.
Note on I7: You can select from the drop down list or enter your own description of each luminaire.
Note on J7: Select Source Type from Drop Down list
Note on K7: If you are using track lighting it must comply with 9.1.4. Select the track type from the drop down and enter the wattage per 9.1.4. If using 9.1.4.c1, enter 30 in the Watts column. If using 9.1.4.c2, enter the VA rating of the circuit breaker and remember to use a quantity of 1 on the Compliance Worksheet. If using 9.1.4.c3, enter the VA rating of the current limiter and remember to use a quantity of 1 on the Compliance Worksheet. If using 9.1.4.d, enter the maximum transformer wattage and remember to use a quantity of 1 on the Compliance Worksheet.
Note on L7: Enter the Watts per Fixture, the Watts per Linear Foot of the luminaire. Track wattage calculeted to the right.
9.4.2 Exit Signs
Exit Sign
Create Luminaire Schedule
Return to Compliance Main Page
Compliance Main Page
Top of Page
Exit Sign
Luminaire Schedule

## Building Area Method
|  |  | Quick Links |  | ASHRAE/IES 90.1-2010 Lighting Compliance Documentation (v3.1)
9.6 Building Area Method for Interior Lighting
90.1-2010
[8 empty] | TOTAL: | 0 | [11 empty] | Compliant | Non Compliant
| Installed Interior Base Lighting | [8 empty] | Lighting Controls
| Building Area |  | Daylighted Areas | Luminaire Type |  | Quantity | Source Type | Watts | Total Watts | Select a Standard Control from the drop down list or you may enter a no-standard control by just typing it in the cell below | Does Control comply with 9.4.1.1 Auto Shutoff? | Does Control comply with 9.4.1.2(a) "Space Control - Bi-Level"? | Does Control comply with 9.4.1.2(b) "Space Control - Occupancy Sensor"? | Does Control comply with 9.4.1.2(c) "Space Control"? | Does Control comply with 9.4.1.4 "Automatic Daylighting Controls for Primary Sidelighted Areas"? | Does Control comply with 9.4.1.5 "Automatic Daylighting Controls for Toplighting"? | Does Control comply with 9.4.1.6 "Additional Control"? | Not Used | Not Used | Does Control comply with 9.4.1.3 "Parking Garage"? | Are Controls Complete?
| In the yellow cells below select from Drop Down one of the spaces on the Interior Room Schedule page. |  | Is the space daylighted as defined in
|  |  |  | Select from Drop Down of Luminaire Schedule |  | Enter the Number of Luminaires or Linear Feet |  | Per Luminaire or Linear Foot
|  |  | or | [21 empty] | Link to 2010 - 9.4.1.1 | Link to 2010 - 9.4.1.2(a) | Link to 2010 - 9.4.1.2(b) | Link to 2010 - 9.4.1.2(c) | Link to 2010 - 9.4.1.4 | Link to 2010 - 9.4.1.5 | Link to 2010 - 9.4.1.6 | 2010 Not Used | 2010 Not Used | Link to 2010 - 9.4.1.3
1 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
13 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
16 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
17 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
18 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
20 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
21 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
22 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
23 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
24 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
25 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[23 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[11 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ''Building Area Method" Building Type |  | Lighting Power Allowance (Watts) | LPD Allowance (watts per sq.ft) |  | Building Area (sq.ft)
0
0
0
0
0
0
0
0
0
0
|  | TOTAL: | 0 | [10 empty] | 0.6
Go to 9.5 Building Area Method Requirements
Link to 9.4.2
Exit Sign Requirements
9.4.1.4 Primary Sidelighted Areas
9.4.1.5 Toplighting
Top of Page
Building Area Method Room Schedule
Compliance Main Page

## Space by Space (step-a)
|  | Quick Links |  | ASHRAE/IES 90.1-2010 Lighting Compliance Documentation (v3.1) | [8 empty] | Retail Area 1 | = the floor area for all products not listed in Retail Areas 2, 3, or 4
|  |  |  | 9.6 Space by Space Method for Interior Lighting | [8 empty] | Retail Area 2 | = the floor area used for the sale of vehicles, sporting goods, and small electronics
|  | Space by Space |  | Lighting Power Allowance | [8 empty] | Retail Area 3 | = the floor area used for the sale of furniture, clothing, cosmetics, and artwork
[13 empty] | Retail Area 4 | = the floor area used for the sale of jewelry, crystal, and china
90.1-2010
This is Space by Space (step 8a) - Calculates the Allowed Watts
|  |  | Base Lighting | [6 empty] | 9.6.2a Decorative Lighting |  |  | 9.6.2b Retail Lighting
0
|  |  | 0 | [5 empty] | 0 |  |  | 0 |  | 0 |  | 0 | 0 | 0
| Space |  | Space Area (sq.ft) |  | LPD Allow. (watts per sq.ft) | RCR Threshold | Leave blank for standard RCR or Enter Claculated RCR | RCR / Corridor factor | Base Lighting Power Allowance (Watts) | Will Decorative Lighting be installed (Yes, No)? | Enter the Decorative Area of each space (sq.ft) | Possible Decorative Watts | Will Retail Display Lighting be installed? | Retail Display Area of each space (sq.ft) | Retail Area Type? | Retail Area Display Allowed Watts | 9.6.2c Control Watts | Possible Space Lighting Power Allowance (Watts) | Atrium Space Height (ft) | Space | Space | Decorative | 0 |  | Allowed | Installed |  | Retail | 0
1 | [7 empty] | 1 | 0 |  |  | 0 | [6 empty] | 0 |  |  |  |  | #VALUE! |  |  | 0 |  |  | #VALUE!
2 | [7 empty] | 1 | 0 |  |  | 0 | [6 empty] | 0 |  |  |  |  | #VALUE! |  |  | 0 |  |  | #VALUE!
3 | [7 empty] | 1 | 0 |  |  | 0 | [6 empty] | 0 |  |  |  |  | #VALUE! |  |  | 0 |  |  | #VALUE!
4 | [7 empty] | 1 | 0 |  |  | 0 | [6 empty] | 0 |  |  |  |  | #VALUE! |  |  | 0 |  |  | #VALUE!
5 | [7 empty] | 1 | 0 |  |  | 0 | [6 empty] | 0 |  |  |  |  | #VALUE! |  |  | 0 |  |  | #VALUE!
6 | [7 empty] | 1 | 0 |  |  | 0 | [6 empty] | 0 |  |  |  |  | #VALUE! |  |  | 0 |  |  | #VALUE!
7 | [7 empty] | 1 | 0 |  |  | 0 | [6 empty] | 0 |  |  |  |  | #VALUE! |  |  | 0 |  |  | #VALUE!
8 | [7 empty] | 1 | 0 |  |  | 0 | [6 empty] | 0 |  |  |  |  | #VALUE! |  |  | 0 |  |  | #VALUE!
9 | [7 empty] | 1 | 0 |  |  | 0 | [6 empty] | 0 |  |  |  |  | #VALUE! |  |  | 0 |  |  | #VALUE!
10 | [7 empty] | 1 | 0 |  |  | 0 | [6 empty] | 0 |  |  |  |  | #VALUE! |  |  | 0 |  |  | #VALUE!
11 | [7 empty] | 1 | 0 |  |  | 0 | [6 empty] | 0 |  |  |  |  | #VALUE! |  |  | 0 |  |  | #VALUE!
12 | [7 empty] | 1 | 0 |  |  | 0 | [6 empty] | 0 |  |  |  |  | #VALUE! |  |  | 0 |  |  | #VALUE!
13 | [7 empty] | 1 | 0 |  |  | 0 | [6 empty] | 0 |  |  |  |  | #VALUE! |  |  | 0 |  |  | #VALUE!
14 | [7 empty] | 1 | 0 |  |  | 0 | [6 empty] | 0 |  |  |  |  | #VALUE! |  |  | 0 |  |  | #VALUE!
15 | [7 empty] | 1 | 0 |  |  | 0 | [6 empty] | 0 |  |  |  |  | #VALUE! |  |  | 0 |  |  | #VALUE!
16 | [7 empty] | 1 | 0 |  |  | 0 | [6 empty] | 0 |  |  |  |  | #VALUE! |  |  | 0 |  |  | #VALUE!
17 | [7 empty] | 1 | 0 |  |  | 0 | [6 empty] | 0 |  |  |  |  | #VALUE! |  |  | 0 |  |  | #VALUE!
18 | [7 empty] | 1 | 0 |  |  | 0 | [6 empty] | 0 |  |  |  |  | #VALUE! |  |  | 0 |  |  | #VALUE!
19 | [7 empty] | 1 | 0 |  |  | 0 | [6 empty] | 0 |  |  |  |  | #VALUE! |  |  | 0 |  |  | #VALUE!
20 | [7 empty] | 1 | 0 |  |  | 0 | [6 empty] | 0 |  |  |  |  | #VALUE! |  |  | 0 |  |  | #VALUE!
21 | [7 empty] | 1 | 0 |  |  | 0 | [6 empty] | 0 |  |  |  |  | #VALUE! |  |  | 0 |  |  | #VALUE!
22 | [7 empty] | 1 | 0 |  |  | 0 | [6 empty] | 0 |  |  |  |  | #VALUE! |  |  | 0 |  |  | #VALUE!
23 | [7 empty] | 1 | 0 |  |  | 0 | [6 empty] | 0 |  |  |  |  | #VALUE! |  |  | 0 |  |  | #VALUE!
24 | [7 empty] | 1 | 0 |  |  | 0 | [6 empty] | 0 |  |  |  |  | #VALUE! |  |  | 0 |  |  | #VALUE!
25 | [7 empty] | 1 | 0 |  |  | 0 | [6 empty] | 0 |  |  |  |  | #VALUE! |  |  | 0 |  |  | #VALUE!
26 | [7 empty] | 1 | 0 |  |  | 0 | [6 empty] | 0 |  |  |  |  | #VALUE! |  |  | 0 |  |  | #VALUE!
27 | [7 empty] | 1 | 0 |  |  | 0 | [6 empty] | 0 |  |  |  |  | #VALUE! |  |  | 0 |  |  | #VALUE!
28 | [7 empty] | 1 | 0 |  |  | 0 | [6 empty] | 0 |  |  |  |  | #VALUE! |  |  | 0 |  |  | #VALUE!
29 | [7 empty] | 1 | 0 |  |  | 0 | [6 empty] | 0 |  |  |  |  | #VALUE! |  |  | 0 |  |  | #VALUE!
30 | [7 empty] | 1 | 0 |  |  | 0 | [6 empty] | 0 |  |  |  |  | #VALUE! |  |  | 0 |  |  | #VALUE!
31 | [7 empty] | 1 | 0 |  |  | 0 | [6 empty] | 0 |  |  |  |  | #VALUE! |  |  | 0 |  |  | #VALUE!
32 | [7 empty] | 1 | 0 |  |  | 0 | [6 empty] | 0 |  |  |  |  | #VALUE! |  |  | 0 |  |  | #VALUE!
33 | [7 empty] | 1 | 0 |  |  | 0 | [6 empty] | 0 |  |  |  |  | #VALUE! |  |  | 0 |  |  | #VALUE!
34 | [7 empty] | 1 | 0 |  |  | 0 | [6 empty] | 0 |  |  |  |  | #VALUE! |  |  | 0 |  |  | #VALUE!
35 | [7 empty] | 1 | 0 |  |  | 0 | [6 empty] | 0 |  |  |  |  | #VALUE! |  |  | 0 |  |  | #VALUE!
36 | [7 empty] | 1 | 0 |  |  | 0 | [6 empty] | 0 |  |  |  |  | #VALUE! |  |  | 0 |  |  | #VALUE!
37 | [7 empty] | 1 | 0 |  |  | 0 | [6 empty] | 0 |  |  |  |  | #VALUE! |  |  | 0 |  |  | #VALUE!
38 | [7 empty] | 1 | 0 |  |  | 0 | [6 empty] | 0 |  |  |  |  | #VALUE! |  |  | 0 |  |  | #VALUE!
39 | [7 empty] | 1 | 0 |  |  | 0 | [6 empty] | 0 |  |  |  |  | #VALUE! |  |  | 0 |  |  | #VALUE!
40 | [7 empty] | 1 | 0 |  |  | 0 | [6 empty] | 0 |  |  |  |  | #VALUE! |  |  | 0 |  |  | #VALUE!
41 | [7 empty] | 1 | 0 |  |  | 0 | [6 empty] | 0 |  |  |  |  | #VALUE! |  |  | 0 |  |  | #VALUE!
42 | [7 empty] | 1 | 0 |  |  | 0 | [6 empty] | 0 |  |  |  |  | #VALUE! |  |  | 0 |  |  | #VALUE!
43 | [7 empty] | 1 | 0 |  |  | 0 | [6 empty] | 0 |  |  |  |  | #VALUE! |  |  | 0 |  |  | #VALUE!
44 | [7 empty] | 1 | 0 |  |  | 0 | [6 empty] | 0 |  |  |  |  | #VALUE! |  |  | 0 |  |  | #VALUE!
45 | [7 empty] | 1 | 0 |  |  | 0 | [6 empty] | 0 |  |  |  |  | #VALUE! |  |  | 0 |  |  | #VALUE!
46 | [7 empty] | 1 | 0 |  |  | 0 | [6 empty] | 0 |  |  |  |  | #VALUE! |  |  | 0 |  |  | #VALUE!
47 | [7 empty] | 1 | 0 |  |  | 0 | [6 empty] | 0 |  |  |  |  | #VALUE! |  |  | 0 |  |  | #VALUE!
48 | [7 empty] | 1 | 0 |  |  | 0 | [6 empty] | 0 |  |  |  |  | #VALUE! |  |  | 0 |  |  | #VALUE!
49 | [7 empty] | 1 | 0 |  |  | 0 | [6 empty] | 0 |  |  |  |  | #VALUE! |  |  | 0 |  |  | #VALUE!
50 | [7 empty] | 1 | 0 |  |  | 0 | [6 empty] | 0 |  |  |  |  | #VALUE! |  |  | 0 |  |  | #VALUE!
Note on K14: To calculate the Actual RCR of a space click on RCR Calculator above for help. Enter width for corridors.
Note on N14: If Decorative Lighting will be installed in addition to general lighting it must meet 9.6.2 Additional Interior Lighting Power and control requirements?
Note on O14: Decorative area must be equal to or less than the Space Area.
Note on P14: If Cell below says "sq.ft. ERROR" you have entered a larger square footage than the space square footage. Please revise!
Note on T14: If Cell below says "sq.ft. ERROR" you have entered a larger square footage than the space square footage. Please revise!
Link to 9.6 - Interior Power Allowance (Space by Space Method) requirements
Click for Space by Space (step-c)
Click for RCR Calculator
Click for Space by Space (step-d)
Click to review 9.6.2a Additional Interior Lighting Power Requirements
Click to review 9.6.2b Additional Interior Lighting Power Requirements
Compliance Main Page
Top of Page
Step 8b
Step 8c
Step 8d

## Space by Space (step-b)
|  | Quick Links |  | ASHRAE/IES 90.1-2010 Lighting Compliance Documentation (v3.1)
9.6 Space by Space Method for Interior Lighting
|  | Space by Space |  | Installed Interior Lighting
[6 empty] | Allowed LPA | 0
| 90.1-2010 |  |  | This is Space by Space (step 8b) - Installed Luminaire and Control Requirements
[6 empty] | TOTAL: | ERROR | Exceeds allowed wattage! | [20 empty] | Compliant | Non Compliant
| IMPORTANT: Move mouse over this cell! Space |  | Luminaire Type |  | Quantity | Watts | Total Watts | Select a Standard Control or a 9.6.2c Control in the yellow cells below. (or type any other control in the cells below) | Does Control comply with 9.4.1.1 "Auto Shutoff"? |  | Does Control comply with 9.4.1.2(a) "Space Control - Bi-Level"? |  | Does Control comply with 9.4.1.2(b) "Space Control - Occupancy Sensor"? |  | Does Control comply with 9.4.1.2(c) "Space Control"? |  | Does Control comply with 9.4.1.4 "Automatic Daylighting Controls for Primary Sidelighted Areas"? |  | Does Control comply with 9.4.1.5 "Automatic Daylighting Controls for Toplighting"? |  | Does Control comply with 9.4.1.6 "Additional Control"? |  | Not Used |  | Not Used |  | Does Control comply with 9.4.1.3 "Parking Garage"? | [10 empty] | ADD1
[11 empty] | one of these two |  | controls must be | [9 empty] | one of these two |  | controls must be
[11 empty] | "Yes" if ADD1 |  | is listed below | [9 empty] | "Yes" if ADD2 |  | is listed below | [21 empty] | ADD1 | [11 empty] | ADD2
[37 empty] | Link to 2010 - 9.4.1.1 | Link to 2010 - 9.4.1.2(a) | Link to 2010 - 9.4.1.2(b) | Link to 2010 - 9.4.1.2(c) | Link to 2010 - 9.4.1.3 | Link to 2010 - 9.4.1.4 | Link to 2010 - 9.4.1.5 | Link to 2010 - 9.4.1.6 |  |  | Required? | Choice |  |  |  |  | Required? | Choice |  |  |  |  | Required? | Choice |  |  |  |  | Required? | Choice
| In the yellow cells below select from Drop Down one of the spaces created in Step 2 on the Room Schedule page. |  | Select from Drop Down of Luminaire Schedule |  | Enter the Number of Luminaires or Linear Feet | Per Luminaire or Linear Foot | [22 empty] | Are Controls Complete? |  | 9.6.2c Control Method | Control factor | Additional Watts
[35 empty] | Space | Control | 9.4.1.1 | 9.4.1.2(a) | 9.4.1.2(b) | 9.4.1.2(c) | 9.4.1.3 | 9.4.1.4 | 9.4.1.5 | 9.4.1.6 |  |  |  |  | Result | 2016 Result | 2010 Result | Final |  |  | Result | 2016 Result | 2010 Result | Final |  |  | Result | 2016 Result | 2010 Result | Final |  |  | Result | 2016 Result | 2010 Result | Final
1 | [30 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
2 | [30 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
3 | [30 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
4 | [30 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
5 | [30 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
6 | [30 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
7 | [30 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
8 | [30 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
9 | [30 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
10 | [30 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
11 | [30 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
12 | [30 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
13 | [30 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
14 | [30 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
15 | [30 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
16 | [30 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
17 | [30 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
18 | [30 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
19 | [30 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
20 | [30 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
21 | [30 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
22 | [30 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
23 | [30 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
24 | [30 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
25 | [30 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
26 | [30 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
27 | [30 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
28 | [30 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
29 | [30 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
30 | [30 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
31 | [30 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
32 | [30 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
33 | [30 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
34 | [30 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
35 | [30 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
36 | [30 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
37 | [30 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
38 | [30 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
39 | [30 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
40 | [30 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
41 | [30 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
42 | [30 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
43 | [30 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
44 | [30 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
45 | [30 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
46 | [30 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
47 | [30 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
48 | [30 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
49 | [30 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
50 | [30 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
[27 empty] | 0 | [5 empty] | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[10 empty] | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0
Note on B10: NOTE: If using the Space-by-Space method and you want to take advantage of 9.6.2 Additional Lighting allowances enter only the GENERAL lighting in this table. Then enter DECORATIVE lighting in Step 8c below Then enter RETAIL ACCENT lighting in Step 8d below
Compliance Main Page
Top of Page (Step 8b)
Step 8a
Step 8c
Step 8d
Link to 9.4.2
Exit Sign Requirements
Luminaire Type
From Luminaire Schedule
Click for 9.6.2c Control Method definitions

## Space by Space (step-c)
|  | Quick Links | ASHRAE/IES 90.1-2010 Lighting Compliance Documentation (v3.1)
9.6 Space by Space Method for Interior Lighting
|  | Space by Space | 9.6.2b Additional Interior Lighting - Decorative Lighting
| 90.1-2010 |  |  |  |  | Total Watts | Wattage | Controls
|  |  | This is Space by Space (step 8c) - Decorative Lighting |  | TOTAL: | 0 | Compliant | Compliant
| Space ID |  | Allowed Decorative Watts | Number of Luminaires or Linear Feet | Watts Per Luminaire or Linear Foot | Total Watts | Wattage | automatically controlled, separately from the general lighting |  | Controls Compliant
1 | [8 empty] | 0 | 0 |  | 0 | #N/A | 0
2 | [8 empty] | 0 | 0 |  | 0 | #N/A | 0
3 | [8 empty] | 0 | 0 |  | 0 | #N/A | 0
4 | [8 empty] | 0 | 0 |  | 0 | #N/A | 0
5 | [8 empty] | 0 | 0 |  | 0 | #N/A | 0
6 | [8 empty] | 0 | 0 |  | 0 | #N/A | 0
7 | [8 empty] | 0 | 0 |  | 0 | #N/A | 0
8 | [8 empty] | 0 | 0 |  | 0 | #N/A | 0
9 | [8 empty] | 0 | 0 |  | 0 | #N/A | 0
10 | [8 empty] | 0 | 0 |  | 0 | #N/A | 0
11 | [8 empty] | 0 | 0 |  | 0 | #N/A | 0
12 | [8 empty] | 0 | 0 |  | 0 | #N/A | 0
13 | [8 empty] | 0 | 0 |  | 0 | #N/A | 0
14 | [8 empty] | 0 | 0 |  | 0 | #N/A | 0
15 | [8 empty] | 0 | 0 |  | 0 | #N/A | 0
16 | [8 empty] | 0 | 0 |  | 0 | #N/A | 0
17 | [8 empty] | 0 | 0 |  | 0 | #N/A | 0
18 | [8 empty] | 0 | 0 |  | 0 | #N/A | 0
19 | [8 empty] | 0 | 0 |  | 0 | #N/A | 0
20 | [8 empty] | 0 | 0 |  | 0 | #N/A | 0
21 | [8 empty] | 0 | 0 |  | 0 | #N/A | 0
22 | [8 empty] | 0 | 0 |  | 0 | #N/A | 0
23 | [8 empty] | 0 | 0 |  | 0 | #N/A | 0
24 | [8 empty] | 0 | 0 |  | 0 | #N/A | 0
25 | [8 empty] | 0 | 0 |  | 0 | #N/A | 0
26 | [8 empty] | 0 | 0 |  | 0 | #N/A | 0
27 | [8 empty] | 0 | 0 |  | 0 | #N/A | 0
28 | [8 empty] | 0 | 0 |  | 0 | #N/A | 0
29 | [8 empty] | 0 | 0 |  | 0 | #N/A | 0
30 | [8 empty] | 0 | 0 |  | 0 | #N/A | 0
31 | [8 empty] | 0 | 0 |  | 0 | #N/A | 0
32 | [8 empty] | 0 | 0 |  | 0 | #N/A | 0
33 | [8 empty] | 0 | 0 |  | 0 | #N/A | 0
34 | [8 empty] | 0 | 0 |  | 0 | #N/A | 0
35 | [8 empty] | 0 | 0 |  | 0 | #N/A | 0
36 | [8 empty] | 0 | 0 |  | 0 | #N/A | 0
37 | [8 empty] | 0 | 0 |  | 0 | #N/A | 0
38 | [8 empty] | 0 | 0 |  | 0 | #N/A | 0
39 | [8 empty] | 0 | 0 |  | 0 | #N/A | 0
40 | [8 empty] | 0 | 0 |  | 0 | #N/A | 0
41 | [8 empty] | 0 | 0 |  | 0 | #N/A | 0
42 | [8 empty] | 0 | 0 |  | 0 | #N/A | 0
43 | [8 empty] | 0 | 0 |  | 0 | #N/A | 0
44 | [8 empty] | 0 | 0 |  | 0 | #N/A | 0
45 | [8 empty] | 0 | 0 |  | 0 | #N/A | 0
46 | [8 empty] | 0 | 0 |  | 0 | #N/A | 0
47 | [8 empty] | 0 | 0 |  | 0 | #N/A | 0
48 | [8 empty] | 0 | 0 |  | 0 | #N/A | 0
49 | [8 empty] | 0 | 0 |  | 0 | #N/A | 0
50 | [8 empty] | 0 | 0 |  | 0 | #N/A | 0
[10 empty] | Compliant |  | Compliant
[10 empty] | 0 | Compliant | 0
Compliance Main Page
Top of Page (Step 8c)
Step 8a
Step 8b
Step 8d
Link to 9.6.2b Additional Interior Lighting Power Requirements
Luminaire Type
From Luminaire Schedule

## Space by Space (step-d)
|  | Quick Links | ASHRAE/IES 90.1-2010 Lighting Compliance Documentation (v3.1)
9.6 Space by Space Method for Interior Lighting
|  | Space by Space | 9.6.2b Additional Interior Lighting - Retail Lighting
| 90.1-2010 |  |  |  |  | Total Watts | Wattage | Controls
|  |  | This is Space by Space (step 8d) - Additional Retail Lighting |  | TOTAL: | 0 | Compliant | Compliant | 0
| Space ID |  | Allowed Retail Watts | Number of Luminaires or Linear Feet | Watts Per Luminaire or Linear Foot | Total Watts | Wattage | automatically controlled, separately from the general lighting | Base Remaining |  | Controls Compliant
1 | [8 empty] | 0 | 0 | 0 |  | 0 | #N/A
2 | [8 empty] | 0 | 0 | 0 |  | 0 | #N/A
3 | [8 empty] | 0 | 0 | 0 |  | 0 | #N/A
4 | [8 empty] | 0 | 0 | 0 |  | 0 | #N/A
5 | [8 empty] | 0 | 0 | 0 |  | 0 | #N/A
6 | [8 empty] | 0 | 0 | 0 |  | 0 | #N/A
7 | [8 empty] | 0 | 0 | 0 |  | 0 | #N/A
8 | [8 empty] | 0 | 0 | 0 |  | 0 | #N/A
9 | [8 empty] | 0 | 0 | 0 |  | 0 | #N/A
10 | [8 empty] | 0 | 0 | 0 |  | 0 | #N/A
11 | [8 empty] | 0 | 0 | 0 |  | 0 | #N/A
12 | [8 empty] | 0 | 0 | 0 |  | 0 | #N/A
13 | [8 empty] | 0 | 0 | 0 |  | 0 | #N/A
14 | [8 empty] | 0 | 0 | 0 |  | 0 | #N/A
15 | [8 empty] | 0 | 0 | 0 |  | 0 | #N/A
16 | [8 empty] | 0 | 0 | 0 |  | 0 | #N/A
17 | [8 empty] | 0 | 0 | 0 |  | 0 | #N/A
18 | [8 empty] | 0 | 0 | 0 |  | 0 | #N/A
19 | [8 empty] | 0 | 0 | 0 |  | 0 | #N/A
20 | [8 empty] | 0 | 0 | 0 |  | 0 | #N/A
21 | [8 empty] | 0 | 0 | 0 |  | 0 | #N/A
22 | [8 empty] | 0 | 0 | 0 |  | 0 | #N/A
23 | [8 empty] | 0 | 0 | 0 |  | 0 | #N/A
24 | [8 empty] | 0 | 0 | 0 |  | 0 | #N/A
25 | [8 empty] | 0 | 0 | 0 |  | 0 | #N/A
26 | [8 empty] | 0 | 0 | 0 |  | 0 | #N/A
27 | [8 empty] | 0 | 0 | 0 |  | 0 | #N/A
28 | [8 empty] | 0 | 0 | 0 |  | 0 | #N/A
29 | [8 empty] | 0 | 0 | 0 |  | 0 | #N/A
30 | [8 empty] | 0 | 0 | 0 |  | 0 | #N/A
31 | [8 empty] | 0 | 0 | 0 |  | 0 | #N/A
32 | [8 empty] | 0 | 0 | 0 |  | 0 | #N/A
33 | [8 empty] | 0 | 0 | 0 |  | 0 | #N/A
34 | [8 empty] | 0 | 0 | 0 |  | 0 | #N/A
35 | [8 empty] | 0 | 0 | 0 |  | 0 | #N/A
36 | [8 empty] | 0 | 0 | 0 |  | 0 | #N/A
37 | [8 empty] | 0 | 0 | 0 |  | 0 | #N/A
38 | [8 empty] | 0 | 0 | 0 |  | 0 | #N/A
39 | [8 empty] | 0 | 0 | 0 |  | 0 | #N/A
40 | [8 empty] | 0 | 0 | 0 |  | 0 | #N/A
41 | [8 empty] | 0 | 0 | 0 |  | 0 | #N/A
42 | [8 empty] | 0 | 0 | 0 |  | 0 | #N/A
43 | [8 empty] | 0 | 0 | 0 |  | 0 | #N/A
44 | [8 empty] | 0 | 0 | 0 |  | 0 | #N/A
45 | [8 empty] | 0 | 0 | 0 |  | 0 | #N/A
46 | [8 empty] | 0 | 0 | 0 |  | 0 | #N/A
47 | [8 empty] | 0 | 0 | 0 |  | 0 | #N/A
48 | [8 empty] | 0 | 0 | 0 |  | 0 | #N/A
49 | [8 empty] | 0 | 0 | 0 |  | 0 | #N/A
50 | [8 empty] | 0 | 0 | 0 |  | 0 | #N/A
[11 empty] | Compliant |  | Compliant
[11 empty] | 0 | Compliant | 0
Luminaire Type
From Luminaire Schedule
Link to 9.6.2b Additional Interior Lighting Power Requirements
Compliance Main Page
Top of Page (Step 8d)
Step 8a
Step 8b
Step 8c

## Exterior
|  |  | Quick Links |  |  | ASHRAE/IES 90.1-2010 Lighting Compliance Documentation (v3.1)
Exterior Lighting Power
[13 empty] | Step 9a: Tradable Areas | Compliant
[13 empty] | Step 9b: NonTradable Areas | Non-Compliant
90.1-2010
| Step 9a: | Installed Exterior Lighting Power | [7 empty] | #VALUE!
[10 empty] | 0 |  |  |  | Compliant
| Installed Exterior Lighting Power (Tradable) see NonTradable below also |  |  |  | Luminaire Type |  | Source Type | Number of Luminaires or Linear Feet | Watts Per Luminaire or Linear Foot | Total Watts | Installed Control In the yellow cells below select a control type or type Control Device. |  |  | Exterior Controls compliant?
1 | [15 empty] | 0 | 0
2 | [15 empty] | 0 | 0
3 | [15 empty] | 0 | 0
4 | [15 empty] | 0 | 0
5 | [15 empty] | 0 | 0
6 | [15 empty] | 0 | 0
7 | [15 empty] | 0 | 0
8 | [15 empty] | 0 | 0
9 | [15 empty] | 0 | 0
10 | [15 empty] | 0 | 0
11 | [15 empty] | 0 | 0
12 | [15 empty] | 0 | 0
13 | [15 empty] | 0 | 0
14 | [15 empty] | 0 | 0
15 | [15 empty] | 0 | 0
16 | [15 empty] | 0 | 0
17 | [15 empty] | 0 | 0
18 | [15 empty] | 0 | 0
19 | [15 empty] | 0 | 0
20 | [15 empty] | 0 | 0
| Step 9b: | Installed Exterior Lighting Power | [7 empty] | Compliant
[10 empty] | 0 |  |  |  | Non-Compliant
| Installed Exterior Lighting Power (NonTradable) see Tradable above also |  |  |  | Luminaire Type |  | Source Type | Number of Luminaires | Watts Per Luminaire or Linear Foot | Total Watts | Installed Control In the yellow cells below select a control type or type Control Device. |  |  | Exterior Controls compliant?
1 | 1 - L2 Window Lights (Drive-through windows/doors (per drive through)) |  |  |  | 24 - Cove |  | #N/A |  | #N/A |  | Astronomical Time Switch |  | YES |  |  | 0 | 1
2 | [15 empty] | 0 | 0
3 | [15 empty] | 0 | 0
4 | [15 empty] | 0 | 0
5 | [15 empty] | 0 | 0
6 | [15 empty] | 0 | 0
7 | [15 empty] | 0 | 0
8 | [15 empty] | 0 | 0
9 | [15 empty] | 0 | 0
10 | [15 empty] | 0 | 0
11 | [15 empty] | 0 | 0
12 | [15 empty] | 0 | 0
13 | [15 empty] | 0 | 0
14 | [15 empty] | 0 | 0
15 | [15 empty] | 0 | 0
16 | [15 empty] | 0 | 0
17 | [15 empty] | 0 | 0
18 | [15 empty] | 0 | 0
19 | [15 empty] | 0 | 0
20 | [15 empty] | 0 | 0
| Step 10: | Exterior Lighting Power Allowance |  |  |  | LZ0 - Undeveloped areas within national parks, state parks, forest land, rural areas, and other undeveloped areas as defined by the authority having jurisdiction
LZ1 - Developed areas of national parks, state parks, forest land, and rural areas
LZ2 - Areas predominantly consisting of residential zoning, neighborhood business districts, light industrial with limited nighttime use and residential mixed use areas
LZ3 - All other areas
LZ4 - High activity commercial districts in major metropolitan areas as designated by the local jurisdiction
|  |  | Select Appropriate Lighting Zone: | 0 |  | #N/A
Base Allowance:
| Step 10a: | Determine the Exterior Lighting Power Allowance - Tradable Surfaces
| Exterior Lighting Power (Tradable) |  |  |  | Area (sq.ft) |  | LPD Allow. (watts per sq.ft) | Tradable Lighting Power Allowance (Watts) | Tradable Watts Installed | Wattage over Allowed Watts | Base Allowance | Installaed - base | Base Wattage remaining for NonTradable | Total Tradable + Base watts used
[8 empty] | 0 | 0 |  |  | #VALUE!
[8 empty] | 0 | 0
[8 empty] | 0 | 0
[8 empty] | 0 | 0
[8 empty] | 0 | 0
[8 empty] | 0 | 0
[8 empty] | 0 | 0
[8 empty] | 0 | 0
[8 empty] | 0 | 0
[8 empty] | 0 | 0
[8 empty] | 0 | 0
[8 empty] | 0 | 0 | 0 |  | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[9 empty] | None Installed |  |  | #VALUE! |  | #VALUE!
| Exterior Lighting Power (NonTradable) |  |  |  | Area (sq.ft) |  | LPD Allow. (watts per sq.ft) | NonTradable Lighting Power Allowance (Watts) | NonTradable Watts Installed | Is Area compliant on its own? | Wattage over allowance | Wattage over with remaining Base Allowance | Is Area compliant with allowed Base Allowance? | Remaining Base Allowance after Tradable Areas
[8 empty] | 0 | 0 |  | 0 |  |  | #VALUE! |  | 0
[8 empty] | 0 | 0 |  | 0 |  |  |  |  | 0
[8 empty] | 0 | 0 |  | 0 |  |  |  |  | 0
[8 empty] | 0 | 0 |  | 0 |  |  |  |  | 0
[8 empty] | 0 | 0 |  | 0 |  |  |  |  | 0
[8 empty] | 0 | 0 |  | 0 |  |  |  |  | 0
[8 empty] | 0 | 0 |  | 0 |  |  |  |  | 0
[8 empty] | 0 | 0 |  | 0 |  |  |  |  | 0
[8 empty] | 0 | 0 |  | 0 |  |  |  |  | 0
[8 empty] | 0 | 0 |  | 0 |  |  |  |  | 0
[8 empty] | 0 | 0 |  | 0 |  |  |  |  | 0
[8 empty] | 0 | 0 | 0 |  |  | Compliant |  |  | 0
#REF!
#REF!
#REF!
1
Top of Page
9.4.3 - Exterior Lighting Power Allowance
9.4.3 - Exterior Lighting Tables
Complies with 9.4.1.7 Control Requirements
Complies with 9.4.1.7 Control Requirements
Compliance Main Page
Tradable Areas
NonTradable Areas

## RCR Calculator
RCR Calculator
Enter these three values:
| Length of the Room Perimeter | Area of the Room | Room Cavity Height | RCR
9.6.3 Room Geometry Adjustment |  |  |  |  | Example:
9.6.3 Room Geometry Adjustment. When using the space by space method, an adjustment of the space LPD is allowed for individual spaces where the Room Cavity Ratio (RCR) calculated for the empty room is documented to be greater than the RCR threshold for that space type shown in Table 9.6.1. RCR = 2.5 × Room Cavity Height × room perimeter length/room area Where: Room Cavity Height = Luminaire mounting height – Workplane For corridor/transition spaces, this adjustment is allowed when the corridor is less than 8 ft wide, regardless of the RCR. The LPD allowance for these spaces may be increased by the following amount: LPD increase = Base space LPD × 0.20 Where: Base space LPD = the applicable LPD from Table 9.6.1.
[5 empty] | Length: | 40
[5 empty] | Area: | 80
[5 empty] | Room Cavity Height: | 7
[5 empty] | RCR: | 8.75
Workplane Height = 2.5' (desktop)
Luminaires mounted at 9.5'
Return to RCR on Compliance Worksheet
Return Space by Space step a

## 9.4.3 Tables (hidden)
2010 TABLE 9.4.2-1 Exterior Lighting Zones | [6 empty] | 2010 TABLE 9.4.2-1 Exterior Lighting Zones | [6 empty] | 2016 TABLE 9.4.2-1 Exterior Lighting Zones
Lighting Zone | [6 empty] | Lighting Zone | [6 empty] | Lighting Zone
LZ0 | 0 | LZ0 - Undeveloped areas within national parks, state parks, forest land, rural areas, and other undeveloped areas as defined by the authority having jurisdiction |  |  |  |  | LZ0 | 0 | LZ0 - Undeveloped areas within national parks, state parks, forest land, rural areas, and other undeveloped areas as defined by the authority having jurisdiction |  |  |  |  | LZ0 | 0 | LZ0 - Undeveloped areas within national parks, state parks, forest land, rural areas, and other undeveloped areas as defined by the authority having jurisdiction
LZ1 | 500 | LZ1 - Developed areas of national parks, state parks, forest land, and rural areas |  |  |  |  | LZ1 | 500 | LZ1 - Developed areas of national parks, state parks, forest land, and rural areas |  |  |  |  | LZ1 | 350 | LZ1 - Developed areas of national parks, state parks, forest land, and rural areas
LZ2 | 600 | LZ2 - Areas predominantly consisting of residential zoning, neighborhood business districts, light industrial with limited nighttime use and residential mixed use areas |  |  |  |  | LZ2 | 600 | LZ2 - Areas predominantly consisting of residential zoning, neighborhood business districts, light industrial with limited nighttime use and residential mixed use areas |  |  |  |  | LZ2 | 400 | LZ2 - Areas predominantly consisting of residential zoning, neighborhood business districts, light industrial with limited nighttime use and residential mixed use areas
LZ3 | 750 | LZ3 - All other areas |  |  |  |  | LZ3 | 750 | LZ3 - All other areas |  |  |  |  | LZ3 | 500 | LZ3 - All other areas
LZ4 | 1300 | LZ4 - High-activity commercial districts in major metropolitan areas as designated by the local jurisdiction |  |  |  |  | LZ4 | 1300 | LZ4 - High-activity commercial districts in major metropolitan areas as designated by the local jurisdiction |  |  |  |  | LZ4 | 900 | LZ4 - High-activity commercial districts in major metropolitan areas as designated by the local jurisdiction
2010 TABLE 9.4.2-2 Individual Lighting Power Allowances for Building Exteriors | [6 empty] | TABLE 9.4.2-2 Individual Lighting Power Allowances for Building Exteriors | [6 empty] | TABLE 9.4.2-2 Individual Lighting Power Allowances for Building Exteriors
| LZ0 | LZ1 | LZ2 | LZ3 | LZ4 | Units |  | LZ0 | LZ1 | LZ2 | LZ3 | LZ4 | Units |  | LZ0 | LZ1 | LZ2 | LZ3 | LZ4 | Units
Base Allowance | 0 | 500 | 600 | 750 | 1300 | watts | Base Allowance | 0 | 500 | 600 | 750 | 1300 | watts | Base Allowance | 0 | 350 | 400 | 500 | 900 | watts
2010 Base Allowance TRADABLE SURFACES | [6 empty] | TRADABLE SURFACES | [6 empty] | TRADABLE SURFACES
Uncovered parking areas and drives | 0 | 0.04 | 0.06 | 0.1 | 0.13 | sq.ft. | Uncovered parking areas and drives | 0 | 0.04 | 0.06 | 0.1 | 0.13 | sq.ft. | Uncovered parking areas and drives | 0 | 0.03 | 0.04 | 0.06 | 0.08 | sq.ft.
Walkways < 10' wide | 0 | 0.7 | 0.7 | 0.8 | 1 | Linear ft | Walkways < 10' wide | 0 | 0.7 | 0.7 | 0.8 | 1 | Linear ft | Walkways < 10' wide | 0 | 0.5 | 0.5 | 0.6 | 0.7 | Linear ft
Walkways ≥ 10' wide OR plazas | 0 | 0.14 | 0.14 | 0.16 | 0.2 | sq.ft. | Walkways ≥ 10' wide OR plazas | 0 | 0.14 | 0.14 | 0.16 | 0.2 | sq.ft. | Walkways ≥ 10' wide OR plazas | 0 | 0.1 | 0.1 | 0.11 | 0.14 | sq.ft.
0 | 0 | 0 | 0 | 0 | 0 | sq.ft. | [7 empty] | Dining Areas | 0 | 0.65 | 0.65 | 0.75 | 0.95 | sq.ft.
Stairways | 0 | 0.75 | 1 | 1 | 1 | sq.ft. | Stairways | 0 | 0.75 | 1 | 1 | 1 | sq.ft. | Stairways | 0 | 0.6 | 0.7 | 0.7 | 0.7 | sq.ft.
Pedestrian tunnels | 0 | 0.15 | 0.15 | 0.2 | 0.3 | sq.ft. | Pedestrian tunnels | 0 | 0.15 | 0.15 | 0.2 | 0.3 | sq.ft. | Pedestrian tunnels | 0 | 0.12 | 0.12 | 0.14 | 0.21 | sq.ft.
Landscaping | 0 | 0.04 | 0.05 | 0.05 | 0.05 | sq.ft. | Landscaping | 0 | 0.04 | 0.05 | 0.05 | 0.05 | sq.ft. | Landscaping | 0 | 0.03 | 0.04 | 0.04 | 0.04 | sq.ft.
Main entries | 0 | 20 | 20 | 30 | 30 | Linear ft | Main entries | 0 | 20 | 20 | 30 | 30 | Linear ft | Pedestrian and vehicular entry/exit | 0 | 14 | 14 | 21 | 21 | Linear ft
Other doors | 0 | 20 | 20 | 20 | 20 | Linear ft | Other doors | 0 | 20 | 20 | 20 | 20 | Linear ft | Entry canopies | 0 | 0.2 | 0.25 | 0.4 | 0.4 | sq.ft.
Entry canopies | 0 | 0.25 | 0.25 | 0.4 | 0.4 | sq.ft. | Entry canopies | 0 | 0.25 | 0.25 | 0.4 | 0.4 | sq.ft. | Loading Docks | 0 | 0.35 | 0.35 | 0.35 | 0.35 | sq.ft.
Sales canopies | 0 | 0.6 | 0.6 | 0.8 | 1 | sq.ft. | Sales canopies | 0 | 0.6 | 0.6 | 0.8 | 1 | sq.ft. | Sales canopies | 0 | 0.4 | 0.4 | 0.6 | 0.7 | sq.ft.
Open sales areas | 0 | 0.25 | 0.25 | 0.5 | 0.7 | sq.ft. | Open sales areas | 0 | 0.25 | 0.25 | 0.5 | 0.7 | sq.ft. | Outdoor Sales - Open areas (including vehicle sales lots) | 0 | 0.2 | 0.2 | 0.35 | 0.5 | sq.ft.
Street frontage | 0 | 0 | 10 | 10 | 30 | Linear ft | Street frontage | 0 | 0 | 10 | 10 | 30 | Linear ft | Street frontage for vehicle sales lots | 0 | 0 | 7 | 7 | 21 | Linear ft
2010 NONTRADABLE SURFACES | [6 empty] | NONTRADABLE SURFACES | [6 empty] | NONTRADABLE SURFACES
Building facades by area | 0 | 0 | 0.1 | 0.15 | 0.2 | sq.ft | Building facades by area | 0 | 0 | 0.1 | 0.15 | 0.2 | sq.ft | Building facades by area | 0 | 0 | 0.1 | 0.15 | 0.2 | sq.ft
Building facades by length | 0 | 0 | 2.5 | 3.75 | 5 | Linear ft | Building facades by length | 0 | 0 | 2.5 | 3.75 | 5 | Linear ft | Building facades by length | 0 | 0 | 2.5 | 3.75 | 5 | Linear ft
ATMs & night depository location | 0 | 270 | 270 | 270 | 270 | Number of | ATMs & night depository location | 0 | 270 | 270 | 270 | 270 | Number of | ATMs & night depository location | 0 | 270 | 270 | 270 | 270 | Number of
Additional ATMs | 0 | 90 | 90 | 90 | 90 | Number of | Additional ATMs | 0 | 90 | 90 | 90 | 90 | Number of | Additional ATMs | 0 | 90 | 90 | 90 | 90 | Number of
Uncovered entrances & gatehouse inspection facilities at guarded facilities | 0 | 0.75 | 0.75 | 0.75 | 0.75 | sq.ft | Uncovered entrances & gatehouse inspection facilities at guarded facilities | 0 | 0.75 | 0.75 | 0.75 | 0.75 | sq.ft | Uncovered entrances & gatehouse inspection facilities at guarded facilities | 0 | 0.75 | 0.75 | 0.75 | 0.75 | sq.ft
Uncovered loading areas for law enforcement, fire, ambulance, and other emergency service vehicles | 0 | 0.5 | 0.5 | 0.5 | 0.5 | sq.ft | Uncovered loading areas for law enforcement, fire, ambulance, and other emergency service vehicles | 0 | 0.5 | 0.5 | 0.5 | 0.5 | sq.ft | Uncovered loading areas for law enforcement, fire, ambulance, and other emergency service vehicles | 0 | 0.5 | 0.5 | 0.5 | 0.5 | sq.ft
Drive-through windows/doors (per drive through) | 0 | 400 | 400 | 400 | 400 | Number of | Drive-through windows/doors (per drive through) | 0 | 400 | 400 | 400 | 400 | Number of | Drive-through windows/doors (per drive through) | 0 | 400 | 400 | 400 | 400 | Number of
Parking near 24-hour retail entrances | 0 | 800 | 800 | 800 | 800 | Number of | Parking near 24-hour retail entrances | 0 | 800 | 800 | 800 | 800 | Number of | Parking near 24-hour retail entrances | 0 | 800 | 800 | 800 | 800 | Number of
Roadway/parking entry, trail head, and toilet facility, or other locations approved by the authority having jurisdiction. | 60 | 0 | 0 | 0 | 0 | Number of | Roadway/parking entry, trail head, and toilet facility, or other locations approved by the authority having jurisdiction. | 60 | 0 | 0 | 0 | 0 | Number of | Roadway/parking entry, trail head, and toilet facility, or other locations approved by the authority having jurisdiction. | 60 | 0 | 0 | 0 | 0 | Number of
Return to Top of Compliance Worksheet
Link to 9.4.3 Exterior Requirements

## 9.5 Table (hidden)
Table 9.5.1 Lighting Power Density Allowances
Using the Building Area Method
2016 |  |  | 2010 | 2013 | 2016
Building Area Type(a) | LPD, W/ft2 | Building Area Type(a) | LPD, W/ft2 | LPD, W/ft2 | LPD, W/ft2
Automotive Facility | 0.71 | Automotive Facility | 0.82 |  | 0.71
Convention Center | 0.76 | Convention Center | 1.08 |  | 0.76
Courthouse | 0.9 | Courthouse | 1.05 |  | 0.9
Dining: Bar lounge/leisure | 0.9 | Dining: Bar Lounge/Leisure | 0.99 |  | 0.9
Dining: Cafeteria/fast food | 0.79 | Dining: Cafeteria/Fast Food | 0.9 |  | 0.79
Dining: Family | 0.78 | Dining: Family | 0.89 |  | 0.78
Dormitory | 0.61 | Dormitory | 0.61 |  | 0.61
Exercise Center | 0.65 | Exercise Center | 0.88 |  | 0.65
Fire Station | 0.53 | Fire Station | 0.71 |  | 0.53
Gymnasium | 0.68 | Gymnasium | 1 |  | 0.68
Health-care Clinic | 0.82 | Health-care Clinic | 0.87 |  | 0.82
Hospital | 1.05 | Hospital | 1.21 |  | 1.05
Hotel | 0.75 | Hotel | 1 |  | 0.75
Library | 0.78 | Library | 1.18 |  | 0.78
Manufacturing Facility | 0.9 | Manufacturing Facility | 1.11 |  | 0.9
Motel | 0.75 | Motel | 0.88 |  | 0.75
Motion Picture Theater | 0.83 | Motion Picture Theater | 0.83 |  | 0.83
Multifamily | 0.68 | Multifamily | 0.6 |  | 0.68
Museum | 1.06 | Museum | 1.06 |  | 1.06
Office | 0.79 | Office | 0.9 |  | 0.79
Parking Garage | 0.15 | Parking Garage | 0.25 |  | 0.15
Penitentiary | 0.75 | Penitentiary | 0.97 |  | 0.75
Performing Arts Theater | 1.18 | Performing Arts Theater | 1.39 |  | 1.18
Police Station | 0.8 | Police Station | 0.96 |  | 0.8
Post Office | 0.67 | Post Office | 0.87 |  | 0.67
Religious Facility | 0.94 | Religious Facility | 1.05 |  | 0.94
Retail | 1.06 | Retail | 1.4 |  | 1.06
School/University | 0.81 | School/University | 0.99 |  | 0.81
Sports Arena | 0.87 | Sports Arena | 0.78 |  | 0.87
Town hall | 0.8 | Town Hall | 0.92 |  | 0.8
Transportation | 0.61 | Transportation | 0.77 |  | 0.61
Warehouse | 0.48 | Warehouse | 0.66 |  | 0.48
Workshop | 0.9 | Workshop | 1.2 |  | 0.9
a. In cases where both a general building area
type and a specific building area type are listed,
the specific building area type shall apply.

## 9.6 Table (hidden)
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27
2016 Space | 2016 LPD | 2016 RCR | 2016 Local Control (See Section 9.4.1.1[a]) | 2016 Restricted to Manual ON (See Section 9.4.1.1[b]) | 2016 Restricted to Partial Automatic ON (See Section 9.4.1.1[c]) | 2016 Bilevel Lighting Control (See Section 9.4.1.1[d]) | 2016 Automatic Daylight Responsive Controls for Sidelighting (See Section 9.4.1.1[e]6) | 2016 Automatic Daylight Responsive Controls for Toplighting (See Section 9.4.1.1[f]6) | 2016 Automatic Partial OFF (See Section 9.4.1.1[g] [Full Off complies]) | 2016 Automatic Full OFF (See Section 9.4.1.1[h]) | 2016 Scheduled Shutoff (See Section 9.4.1.1[i]) | Garage 9.4.1.2 | 2016 9.6.2c | 2010 Space | 2010 LPD | 2010 RCR | 2010 9.4.1.1 Automatic Lighting Shutoff | 9.4.1.2 Space Control (a) Bi-Level | 9.4.1.2 Space Control (b) Occ | 9.4.1.2 Space Control (c) | 9.4.1.3 Parking Garage Lighting Control | 9.4.1.4 Automatic Daylighting Controls for Primary Sidelighted Areas | 9.4.1.5 Automatic Daylighting Controls for Toplighting | 9.4.1.6 Additional Control | 2010 9.6.2c | Not Used - leave blank
Atrium <20 ft in height | 0.03 | NA | REQ | ADD1 | ADD1 | NA | REQ | REQ | NA | ADD2 | ADD2 | NA | Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage | Atrium - First 40 ft in height | 0.03 | NA | REQ | NA | NA | REQ | NA | Check 9.4.1.4 | Check 9.4.1.5 | Check 9.4.1.6 | Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage
Atrium >=20 ft and <40 ft in height | 0.03 | NA | REQ | ADD1 | ADD1 | REQ | REQ | REQ | NA | ADD2 | ADD2 | NA | Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage | Atrium - First 40 ft in height | 0.03 | NA | REQ | NA | NA | REQ | NA | Check 9.4.1.4 | Check 9.4.1.5 | Check 9.4.1.6 | Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage
Atrium >40 ft in height | 0.02 | NA | REQ | ADD1 | ADD1 | REQ | REQ | REQ | NA | ADD2 | ADD2 | NA | Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage | Atrium >40 ft in height | 0.02 | NA | REQ | NA | NA | REQ | NA | Check 9.4.1.4 | Check 9.4.1.5 | Check 9.4.1.6 | Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage
Audience Seating Area - All other areas | 0.43 | 4 | REQ | ADD1 | ADD1 | NA | REQ | REQ | NA | ADD2 | ADD2 | NA | NA | Audience Seating Area - All other areas | 0.79 | 4 | REQ | REQ | NA | REQ | NA | Check 9.4.1.4 | Check 9.4.1.5 | Check 9.4.1.6 | NA
Audience Seating Area - Auditorium | 0.63 | 6 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | NA | ADD2 | ADD2 | NA | NA | Audience/Seating Area - Auditorium | 0.79 | 6 | REQ | REQ | NA | REQ | NA | Check 9.4.1.4 | Check 9.4.1.5 | Check 9.4.1.6 | NA
Audience Seating Area - Convention center | 0.82 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | NA | ADD2 | ADD2 | NA | NA | Convention Center - Audience Seating | 0.82 | 4 | REQ | REQ | NA | REQ | NA | Check 9.4.1.4 | Check 9.4.1.5 | Check 9.4.1.6 | NA
Audience Seating Area - Gymnasium | 0.65 | 6 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | NA | ADD2 | ADD2 | NA | NA | Gymnasium/Fitness Center - Gymnasium - Audience Seating | 0.43 | 6 | REQ | REQ | NA | REQ | NA | Check 9.4.1.4 | Check 9.4.1.5 | Check 9.4.1.6 | NA
Audience Seating Area - Motion picture theater | 1.14 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | NA | ADD2 | ADD2 | NA | NA | Audience/Seating Area - Motion Picture Theater | 1.14 | 4 | REQ | REQ | NA | REQ | NA | Check 9.4.1.4 | Check 9.4.1.5 | Check 9.4.1.6 | NA
Audience Seating Area - Penitentiary | 0.28 | 4 | REQ | ADD1 | ADD1 | NA | REQ | REQ | NA | ADD2 | ADD2 | NA | NA | Courthouse/Police Station/Penitentiary - Penitentiary Audience Seating | 0.43 | 4 | REQ | REQ | NA | REQ | NA | Check 9.4.1.4 | Check 9.4.1.5 | Check 9.4.1.6 | NA
Audience Seating Area - Performing arts theater | 2.03 | 8 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | NA | ADD2 | ADD2 | NA | NA | Audience/Seating Area - Performing Arts Theater | 2.43 | 8 | REQ | REQ | NA | REQ | NA | Check 9.4.1.4 | Check 9.4.1.5 | Check 9.4.1.6 | NA
Audience Seating Area - Religious facility | 1.53 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | NA | ADD2 | ADD2 | NA | NA | Religious Buildings - Audience Seating | 1.53 | 4 | REQ | REQ | NA | REQ | NA | Check 9.4.1.4 | Check 9.4.1.5 | Check 9.4.1.6 | NA
Audience Seating Area - Sports arena | 0.43 | 4 | REQ | ADD1 | ADD1 | NA | REQ | REQ | NA | ADD2 | ADD2 | NA | NA | Sports Arena - Audience Seating | 0.43 | 4 | REQ | REQ | NA | REQ | NA | Check 9.4.1.4 | Check 9.4.1.5 | Check 9.4.1.6 | NA
Audience Seating Area - Transportation | 0.43 | 4 | REQ | ADD1 | ADD1 | NA | REQ | REQ | NA | ADD2 | ADD2 | NA | NA | Transportation - Audience Seating | 0.54 | 4 | REQ | REQ | NA | REQ | NA | Check 9.4.1.4 | Check 9.4.1.5 | Check 9.4.1.6 | NA
Banking Activity Area | 0.86 | 6 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | NA | ADD2 | ADD2 | NA | NA | Bank/Office - Banking Activity Area | 1.38 | 6 | REQ | REQ | NA | REQ | NA | Check 9.4.1.4 | Check 9.4.1.5 | Check 9.4.1.6 | NA
Chapel - Facility for the Visually Impaired (used primarily by residents) | 1.06 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | NA | ADD2 | ADD2 | NA | NA |  | Not 2010 | NA | REQ | NA | NA | REQ | NA | Check 9.4.1.4 | Check 9.4.1.5 | Check 9.4.1.6 | NA
Classroom/Lecture Hall/Training Room - All other rooms | 0.92 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | NA | REQ | NA | NA | Conference Room, Meeting Room, Classroom (Lecture/Training) | Classroom/Lecture/Training | 1.24 | 4 | REQ | REQ | REQ | NA | NA | Check 9.4.1.4 | Check 9.4.1.5 | Check 9.4.1.6 | Conference Room, Meeting Room, Classroom (Lecture/Training)
Classroom/Lecture Hall/Training Room - Penitentiary | 1.34 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | NA | REQ | NA | NA | Conference Room, Meeting Room, Classroom (Lecture/Training) | Courthouse/Police Station/Penitentiary - Pentitentiary Classroom | 1.34 | 4 | REQ | REQ | NA | REQ | NA | Check 9.4.1.4 | Check 9.4.1.5 | Check 9.4.1.6 | Conference Room, Meeting Room, Classroom (Lecture/Training)
Computer Room | 1.33 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | NA | ADD2 | ADD2 | NA | NA |  | Not 2010 | NA | REQ | NA | NA | REQ | NA | Check 9.4.1.4 | Check 9.4.1.5 | Check 9.4.1.6 | NA
Conference/Meeting/Multipurpose Room | 1.07 | 6 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | NA | REQ | NA | NA | Conference Room, Meeting Room, Classroom (Lecture/Training) | Conference/Meeting/Multipurpose | 1.23 | 6 | REQ | REQ | REQ | NA | NA | Check 9.4.1.4 | Check 9.4.1.5 | Check 9.4.1.6 | Conference Room, Meeting Room, Classroom (Lecture/Training)
Confinement Cells | 0.81 | 6 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | NA | ADD2 | ADD2 | NA | NA | Courthouse/Police Station/Penitentiary - Confinement Cells | 1.1 | 6 | REQ | REQ | NA | REQ | NA | Check 9.4.1.4 | Check 9.4.1.5 | Check 9.4.1.6 | NA
Convention Center—Exhibit Space | 0.88 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | NA | ADD2 | ADD2 | NA | NA | Convention Center - Exhibit Space | 1.45 | 4 | REQ | REQ | NA | REQ | NA | Check 9.4.1.4 | Check 9.4.1.5 | Check 9.4.1.6 | NA
Copy/Print Room | 0.56 | 6 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | NA | REQ | NA | NA | NA |  | Not 2010 | NA | REQ | NA | NA | REQ | NA | Check 9.4.1.4 | Check 9.4.1.5 | Check 9.4.1.6 | NA
Corridor - All other | 0.66 | width <8 ft | REQ | NA | NA | NA | REQ | REQ | REQ | ADD2 | ADD2 | NA | Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage | Corridor/Transition | 0.66 | 8' wide | REQ | NA | NA | REQ | NA | Check 9.4.1.4 | Check 9.4.1.5 | Check 9.4.1.6 | Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage
Corridor - Facility for the visually impaired not used primarily by the staff | 0.92 | width <8 ft | REQ | NA | NA | NA | REQ | REQ | REQ | ADD2 | ADD2 | NA | Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage |  | Not 2010 | NA | REQ | NA | NA | REQ | NA | Check 9.4.1.4 | Check 9.4.1.5 | Check 9.4.1.6 | Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage
Corridor - Hospital | 0.92 | width <8 ft | REQ | NA | NA | NA | REQ | REQ | ADD2 | ADD2 | ADD2 | NA | Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage | Hospital - Corridor/Transition | 0.89 | 8' wide | REQ | NA | NA | REQ | NA | Check 9.4.1.4 | Check 9.4.1.5 | Check 9.4.1.6 | Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage
Corridor - Manufacturing facility | 0.29 | width <8 ft | REQ | NA | NA | NA | REQ | REQ | NA | ADD2 | ADD2 | NA | Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage | Manufacturing - Corridor/Transition | 0.41 | 8' wide | REQ | NA | NA | REQ | NA | Check 9.4.1.4 | Check 9.4.1.5 | Check 9.4.1.6 | Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage
Courthouse/Police Station/Penitentiary - Judges' Chambers | 0.93 | 8 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | NA | REQ | NA | NA | Private Office | Courthouse/Police Station/Penitentiary - Judges' Chambers | 1.17 | 8 | REQ | REQ | NA | REQ | NA | Check 9.4.1.4 | Check 9.4.1.5 | Check 9.4.1.6 | Private Office
Courtroom | 1.39 | 6 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | NA | ADD2 | ADD2 | NA | NA | Courthouse/Police Station/Penitentiary - Courtroom | 1.72 | 6 | REQ | REQ | NA | REQ | NA | Check 9.4.1.4 | Check 9.4.1.5 | Check 9.4.1.6 | NA
Dining Area - All other dining areas | 0.63 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | NA | ADD2 | ADD2 | NA | Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage | Dining Area | 0.65 | 4 | REQ | REQ | NA | REQ | NA | Check 9.4.1.4 | Check 9.4.1.5 | Check 9.4.1.6 | Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage
Dining Area - Bar/lounge or leisure dining | 0.93 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | NA | ADD2 | ADD2 | NA | Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage | Dining Area - Bar Lounge/Leisure Dining | 1.31 | 4 | REQ | REQ | NA | REQ | NA | Check 9.4.1.4 | Check 9.4.1.5 | Check 9.4.1.6 | Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage
Dining Area - Cafeteria or fast food dining | 0.63 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | NA | ADD2 | ADD2 | NA | Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage | Dining Area - Family Dining | 0.89 | 4 | REQ | REQ | NA | REQ | NA | Check 9.4.1.4 | Check 9.4.1.5 | Check 9.4.1.6 | Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage
Dining Area - Facility for the visually impaired not used primarily by the staff | 2 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | NA | ADD2 | ADD2 | NA | Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage |  | Not 2010 | NA | REQ | NA | NA | REQ | NA | Check 9.4.1.4 | Check 9.4.1.5 | Check 9.4.1.6 | Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage
Dining Area - Family dining | 0.71 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | NA | ADD2 | ADD2 | NA | Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage | Dining Area - Family Dining | 0.89 | 4 | REQ | REQ | NA | REQ | NA | Check 9.4.1.4 | Check 9.4.1.5 | Check 9.4.1.6 | Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage
Dining Area - Hotel/Motel - Highway Lodging | 0.63 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | NA | ADD2 | ADD2 | NA | Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage | Hotel/Motel - Highway Lodging Dining | 0.88 | 4 | REQ | REQ | NA | REQ | NA | Check 9.4.1.4 | Check 9.4.1.5 | Check 9.4.1.6 | Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage
Dining Area - Hotel/Motel - Hotel Dining | 0.63 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | NA | ADD2 | ADD2 | NA | Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage | Hotel/Motel - Hotel Dining | 0.82 | 4 | REQ | REQ | NA | REQ | NA | Check 9.4.1.4 | Check 9.4.1.5 | Check 9.4.1.6 | Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage
Dining Area - Penitentiary | 0.96 | 6 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | NA | ADD2 | ADD2 | NA | Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage | Courthouse/Police Station/Penitentiary - Penitentiary Dining | 1.07 | 6 | REQ | REQ | NA | REQ | NA | Check 9.4.1.4 | Check 9.4.1.5 | Check 9.4.1.6 | Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage
Dormitory—Living Quarters | 0.54 | 8 | REQ | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | Dormitory - Living Quarters | 0.38 | 8 | REQ | REQ | NA | REQ | NA | Check 9.4.1.4 | Check 9.4.1.5 | Check 9.4.1.6 | NA
Electrical/Mechanical Room | 0.43 | 6 | REQ | NA | NA | NA | REQ | REQ | NA | NA | NA | NA | NA | Electrical/Mechanical Room | 0.95 | 6 | REQ | NA | NA | REQ | NA | Check 9.4.1.4 | Check 9.4.1.5 | Check 9.4.1.6 | NA
Emergency Vehicle Garage | 0.41 | 4 | REQ | ADD1 | ADD1 | NA | REQ | REQ | NA | ADD2 | ADD2 | NA | NA | Fire Stations - Engine Room | 0.56 | 4 | REQ | REQ | NA | REQ | NA | Check 9.4.1.4 | Check 9.4.1.5 | Check 9.4.1.6 | NA
Fire Station - Sleeping Quarters | 0.2 | 6 | REQ | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | Fire Stations - Sleeping Quarters | 0.25 | 6 | REQ | REQ | NA | REQ | NA | Check 9.4.1.4 | Check 9.4.1.5 | Check 9.4.1.6 | NA
Food Preparation Area | 1.06 | 6 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | NA | ADD2 | ADD2 | NA | NA | Food Preperation | 0.99 | 6 | REQ | REQ | NA | REQ | NA | Check 9.4.1.4 | Check 9.4.1.5 | Check 9.4.1.6 | NA
Guest Room | 0.77 | 6 | See 9.4.1.3(b) | See 9.4.1.3(b) | See 9.4.1.3(b) | See 9.4.1.3(b) | See 9.4.1.3(b) | See 9.4.1.3(b) | See 9.4.1.3(b) | See 9.4.1.3(b) | See 9.4.1.3(b) | NA | NA |  | Not 2010 | NA | REQ | NA | NA | REQ | NA | Check 9.4.1.4 | Check 9.4.1.5 | Check 9.4.1.6 | NA
Guest Room - Highway Lodging | 0.77 | 6 | See 9.4.1.3(b) | See 9.4.1.3(b) | See 9.4.1.3(b) | See 9.4.1.3(b) | See 9.4.1.3(b) | See 9.4.1.3(b) | See 9.4.1.3(b) | See 9.4.1.3(b) | See 9.4.1.3(b) | NA | NA | Hotel/Motel - Highway Lodging Guest Room | 0.75 | 6 | Check 9.4.1.6 | Check 9.4.1.6 | Check 9.4.1.6 | Check 9.4.1.6 | Check 9.4.1.6 | Check 9.4.1.6 | Check 9.4.1.6 | Check 9.4.1.6 | NA
Guest Room - Hotel Guest Rooms | 0.77 | 6 | See 9.4.1.3(b) | See 9.4.1.3(b) | See 9.4.1.3(b) | See 9.4.1.3(b) | See 9.4.1.3(b) | See 9.4.1.3(b) | See 9.4.1.3(b) | See 9.4.1.3(b) | See 9.4.1.3(b) | NA | NA | Hotel/Motel - Hotel Guest Rooms | 1.11 | 6 | Check 9.4.1.6 | Check 9.4.1.6 | Check 9.4.1.6 | Check 9.4.1.6 | Check 9.4.1.6 | Check 9.4.1.6 | Check 9.4.1.6 | Check 9.4.1.6 | NA
Gymnasium/Fitness Center - Exercise area | 0.5 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | NA | ADD2 | ADD2 | NA | Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage | Gymnasium/Fitness Center - Fitness Area | 0.72 | 4 | REQ | REQ | NA | REQ | NA | Check 9.4.1.4 | Check 9.4.1.5 | Check 9.4.1.6 | Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage
Gymnasium/Fitness Center - Playing area | 0.82 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | NA | ADD2 | ADD2 | NA | Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage | Gymnasium/Fitness Center - Playing Area | 1.2 | 4 | REQ | REQ | NA | REQ | NA | Check 9.4.1.4 | Check 9.4.1.5 | Check 9.4.1.6 | Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage
Healthcare Facility - Emergency | 1.68 | 8 | REQ | NA | NA | REQ | REQ | REQ | NA | ADD2 | ADD2 | NA | NA | Hospital - Emergency | 2.26 | 6 | REQ | REQ | NA | REQ | NA | Check 9.4.1.4 | Check 9.4.1.5 | Check 9.4.1.6 | NA
Healthcare Facility - Exam/treatment room | 1.68 | 8 | REQ | NA | NA | REQ | REQ | REQ | NA | ADD2 | ADD2 | NA | NA | Hospital - Exam/Treatment | 1.66 | 8 | REQ | REQ | NA | REQ | NA | Check 9.4.1.4 | Check 9.4.1.5 | Check 9.4.1.6 | NA
Healthcare Facility - Imaging room | 1.06 | 6 | REQ | NA | NA | REQ | NA | NA | NA | ADD2 | ADD2 | NA | NA | Hospital - Radiology/Imaging | 1.32 | 6 | REQ | REQ | NA | REQ | NA | Check 9.4.1.4 | Check 9.4.1.5 | Check 9.4.1.6 | NA
Healthcare Facility - Medical supply room - All other storage rooms | 0.46 | 6 | REQ | ADD1 | ADD1 | NA | REQ | REQ | REQ | ADD2 | ADD2 | NA | NA | Storage | 0.63 | 6 | REQ | NA | REQ | NA | NA | Check 9.4.1.4 | Check 9.4.1.5 | Check 9.4.1.6 | NA
Healthcare Facility - Medical supply room <50 ft2 | 0.97 | 6 | REQ | NA | NA | NA | NA | NA | NA | ADD2 | ADD2 | NA | NA | Storage | 0.63 | 6 | REQ | NA | REQ | NA | NA | Check 9.4.1.4 | Check 9.4.1.5 | Check 9.4.1.6 | NA
Healthcare Facility - Medical supply room >=50 ft2 and <1000 ft2 | 0.46 | 6 | REQ | ADD1 | ADD1 | NA | REQ | REQ | NA | REQ | NA | NA | NA | Storage | 0.63 | 6 | REQ | NA | REQ | NA | NA | Check 9.4.1.4 | Check 9.4.1.5 | Check 9.4.1.6 | NA
Healthcare Facility - Nurse’s station | 0.81 | 6 | REQ | NA | NA | REQ | REQ | REQ | NA | ADD2 | ADD2 | NA | NA | Hospital - Nurses' Station | 0.87 | 6 | REQ | REQ | NA | REQ | NA | Check 9.4.1.4 | Check 9.4.1.5 | Check 9.4.1.6 | NA
Healthcare Facility - Nursery | 1 | 6 | REQ | NA | NA | REQ | REQ | REQ | NA | ADD2 | ADD2 | NA | NA | Hospital - Nursery | 0.88 | 6 | REQ | REQ | NA | REQ | NA | Check 9.4.1.4 | Check 9.4.1.5 | Check 9.4.1.6 | NA
Healthcare Facility - Operating room | 2.17 | 6 | REQ | NA | NA | REQ | NA | NA | NA | ADD2 | ADD2 | NA | NA | Hospital - Operating Room | 1.89 | 6 | REQ | REQ | NA | REQ | NA | Check 9.4.1.4 | Check 9.4.1.5 | Check 9.4.1.6 | NA
Healthcare Facility - Patient room | 0.62 | 6 | REQ | NA | NA | REQ | REQ | REQ | NA | ADD2 | ADD2 | NA | NA | Hospital - Patient Room | 0.62 | 6 | REQ | REQ | NA | REQ | NA | Check 9.4.1.4 | Check 9.4.1.5 | Check 9.4.1.6 | NA
Healthcare Facility - Physical therapy room | 0.84 | 6 | REQ | NA | NA | REQ | REQ | REQ | NA | ADD2 | ADD2 | NA | NA | Hospital - Physical Therapy | 0.91 | 6 | REQ | REQ | NA | REQ | NA | Check 9.4.1.4 | Check 9.4.1.5 | Check 9.4.1.6 | NA
Healthcare Facility - Recovery room | 1.03 | 6 | REQ | NA | NA | REQ | REQ | REQ | NA | ADD2 | ADD2 | NA | NA | Hospital - Recovery | 1.15 | 6 | REQ | REQ | NA | REQ | NA | Check 9.4.1.4 | Check 9.4.1.5 | Check 9.4.1.6 | NA
Laboratory - All other laboratories | 1.45 | 6 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | NA | ADD2 | ADD2 | NA | NA | Laboratory - Research | 1.81 | 6 | REQ | REQ | NA | REQ | NA | Check 9.4.1.4 | Check 9.4.1.5 | Check 9.4.1.6 | NA
Laboratory - In or as a classroom | 1.2 | 6 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | REQ | ADD2 | ADD2 | NA | Conference Room, Meeting Room, Classroom (Lecture/Training) | Laboratory - Classroom | 1.28 | 6 | REQ | REQ | REQ | NA | NA | Check 9.4.1.4 | Check 9.4.1.5 | Check 9.4.1.6 | Conference Room, Meeting Room, Classroom (Lecture/Training)
Laundry/Washing Area | 0.43 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | NA | ADD2 | ADD2 | NA | NA | Hospital - Laundry - Washing | 0.6 | 4 | REQ | REQ | NA | REQ | NA | Check 9.4.1.4 | Check 9.4.1.5 | Check 9.4.1.6 | NA
Library - Card File & Cataloging | 0.82 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | NA | ADD2 | ADD2 | NA | NA | Library - Card File & Cataloging | 0.72 | 4 | REQ | REQ | NA | REQ | NA | Check 9.4.1.4 | Check 9.4.1.5 | Check 9.4.1.6 | NA
Library - Reading area | 0.82 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | NA | ADD2 | ADD2 | NA | NA | Library - Reading Area | 0.93 | 4 | REQ | REQ | NA | REQ | NA | Check 9.4.1.4 | Check 9.4.1.5 | Check 9.4.1.6 | NA
Library - Stacks | 1.2 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | REQ | ADD2 | ADD2 | NA | NA | Library - Stacks | 1.71 | 4 | REQ | REQ | NA | REQ | NA | Check 9.4.1.4 | Check 9.4.1.5 | Check 9.4.1.6 | NA
Loading Dock, Interior | 0.58 | 6 | REQ | ADD1 | ADD1 | NA | REQ | REQ | NA | ADD2 | ADD2 | NA | NA |  | Not 2010 | NA | REQ | NA | NA | REQ | NA | Check 9.4.1.4 | Check 9.4.1.5 | Check 9.4.1.6 | NA
Lobby - All other lobbies | 1 | 4 | REQ | NA | NA | NA | REQ | REQ | REQ | ADD2 | ADD2 | NA | Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage | Lobby | 0.9 | 4 | REQ | NA | NA | REQ | NA | Check 9.4.1.4 | Check 9.4.1.5 | Check 9.4.1.6 | Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage
Lobby - Elevator | 0.69 | 6 | REQ | NA | NA | NA | REQ | REQ | NA | ADD2 | ADD2 | NA | Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage | Lobby - Elevator | 0.64 | 6 | REQ | NA | NA | REQ | NA | Check 9.4.1.4 | Check 9.4.1.5 | Check 9.4.1.6 | Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage
Lobby - Facility for the visually impaired and not used primarily by the staff | 2.03 | 4 | REQ | NA | NA | NA | REQ | REQ | REQ | ADD2 | ADD2 | NA | Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage |  | Not 2010 | NA | REQ | NA | NA | REQ | NA | Check 9.4.1.4 | Check 9.4.1.5 | Check 9.4.1.6 | Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage
Lobby - Hotel | 1.06 | 4 | REQ | NA | NA | NA | REQ | REQ | NA | ADD2 | ADD2 | NA | Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage | Hotel/Motel - Hotel Lobby | 1.06 | 4 | REQ | NA | NA | REQ | NA | Check 9.4.1.4 | Check 9.4.1.5 | Check 9.4.1.6 | Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage
Lobby - Motion picture theater | 0.45 | 4 | REQ | NA | NA | NA | REQ | REQ | NA | ADD2 | ADD2 | NA | Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage | Lobby - Motion Picture Theater | 0.52 | 4 | REQ | NA | NA | REQ | NA | Check 9.4.1.4 | Check 9.4.1.5 | Check 9.4.1.6 | Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage
Lobby - Performing arts theater | 1.7 | 6 | REQ | NA | NA | NA | REQ | REQ | REQ | ADD2 | ADD2 | NA | Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage | Lobby - Performing Arts Theater | 2 | 6 | REQ | NA | NA | REQ | NA | Check 9.4.1.4 | Check 9.4.1.5 | Check 9.4.1.6 | Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage
Locker Room | 0.48 | 6 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | NA | REQ | NA | NA | NA | Locker Room | 0.75 | 6 | REQ | REQ | REQ | NA | NA | Check 9.4.1.4 | Check 9.4.1.5 | Check 9.4.1.6 | NA
Lounge/Breakroom - All other lounges/breakrooms | 0.62 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | NA | REQ | NA | NA | NA | Lounge/Recreation | 0.73 | 4 | REQ | REQ | REQ | NA | NA | Check 9.4.1.4 | Check 9.4.1.5 | Check 9.4.1.6 | NA
Lounge/Breakroom - Healthcare facility | 0.78 | 6 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | NA | REQ | NA | NA | NA | Hospital - Lounge/Recreation | 1.07 | 6 | REQ | REQ | NA | REQ | NA | Check 9.4.1.4 | Check 9.4.1.5 | Check 9.4.1.6 | NA
Manufacturing Facility - Detailed manufacturing area | 0.93 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | NA | ADD2 | ADD2 | NA | NA | Manufacturing - Detailed Manufacturing | 1.29 | 4 | REQ | REQ | NA | REQ | NA | Check 9.4.1.4 | Check 9.4.1.5 | Check 9.4.1.6 | NA
Manufacturing Facility - Equipment room | 0.65 | 6 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | NA | ADD2 | ADD2 | NA | NA | Manufacturing - Equipment Room | 0.95 | 6 | REQ | REQ | NA | REQ | NA | Check 9.4.1.4 | Check 9.4.1.5 | Check 9.4.1.6 | NA
Manufacturing Facility - Extra high bay area (>50 ft floor-to-ceiling height) | 1.05 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | NA | ADD2 | ADD2 | NA | NA | Manufacturing - Extra High Bay (≥ 50') | 1.05 | 4 | REQ | REQ | NA | REQ | NA | Check 9.4.1.4 | Check 9.4.1.5 | Check 9.4.1.6 | NA
Manufacturing Facility - High bay area (25 to 50 ft floor-to-ceiling height) | 0.75 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | NA | ADD2 | ADD2 | NA | NA | Manufacturing - High Bay (≥ 25' & < 50') | 1.23 | 4 | REQ | REQ | NA | REQ | NA | Check 9.4.1.4 | Check 9.4.1.5 | Check 9.4.1.6 | NA
Manufacturing Facility - Low bay area (<25 ft floor-to-ceiling height) | 0.96 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | NA | ADD2 | ADD2 | NA | NA | Manufacturing - Low Bay (< 25') | 1.19 | 4 | REQ | REQ | NA | REQ | NA | Check 9.4.1.4 | Check 9.4.1.5 | Check 9.4.1.6 | NA
Museum - General exhibition area | 1.05 | 6 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | NA | ADD2 | ADD2 | NA | NA | Museum - General Exhibition | 1.05 | 6 | REQ | REQ | NA | REQ | NA | Check 9.4.1.4 | Check 9.4.1.5 | Check 9.4.1.6 | NA
Museum - Restoration room | 0.85 | 6 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | NA | ADD2 | ADD2 | NA | NA | Museum - Restoration | 1.02 | 6 | REQ | REQ | NA | REQ | NA | Check 9.4.1.4 | Check 9.4.1.5 | Check 9.4.1.6 | NA
Office - Enclosed and <=250 ft2 | 0.93 | 8 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | NA | REQ | NA | NA | Private Office | Office-Enclosed | 1.11 | 8 | REQ | REQ | REQ | NA | NA | Check 9.4.1.4 | Check 9.4.1.5 | Check 9.4.1.6 | Private Office
Office - Enclosed and >250 ft2 | 0.93 | 8 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | NA | ADD2 | ADD2 | NA | Private Office | Office-Enclosed | 1.11 | 8 | REQ | REQ | REQ | NA | NA | Check 9.4.1.4 | Check 9.4.1.5 | Check 9.4.1.6 | Private Office
Office - Open plan | 0.81 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | NA | ADD2 | ADD2 | NA | Open Office | Office-Open | 0.98 | 4 | REQ | REQ | NA | REQ | NA | Check 9.4.1.4 | Check 9.4.1.5 | Check 9.4.1.6 | Open Office
Parking Area, Interior | 0.14 | 4 | See 9.4.1.2 | See 9.4.1.2 | See 9.4.1.2 | See 9.4.1.2 | See 9.4.1.2 | See 9.4.1.2 | See 9.4.1.2 | See 9.4.1.2 | REQ | See 9.4.1.2 | Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage | Parking Garage - Garage Area | 0.19 | 4 | Check 9.4.1.3 | Check 9.4.1.3 | Check 9.4.1.3 | Check 9.4.1.3 | REQ | Check 9.4.1.3 | Check 9.4.1.3 | Check 9.4.1.3 | Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage
Performing Arts Theater - Dressing Room | 0.36 | 6 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | NA | REQ | NA | NA | NA | Dressing/Fitting Room - Performing Arts Theater | 0.4 | 6 | REQ | REQ | REQ | NA | NA | Check 9.4.1.4 | Check 9.4.1.5 | Check 9.4.1.6 | NA
Pharmacy Area | 1.34 | 6 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | NA | ADD2 | ADD2 | NA | NA | Hospital - Pharmacy | 1.14 | 6 | REQ | REQ | NA | REQ | NA | Check 9.4.1.4 | Check 9.4.1.5 | Check 9.4.1.6 | NA
Post Office - Sorting Area | 0.68 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | REQ | ADD2 | ADD2 | NA | NA | Post Office - Sorting Area | 0.94 | 4 | REQ | REQ | NA | REQ | NA | Check 9.4.1.4 | Check 9.4.1.5 | Check 9.4.1.6 | NA
Recreation room/common living room - Facility for the Visually Impaired not used primarily by staff | 1.8 | 6 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | NA | ADD2 | ADD2 | NA | NA |  | Not 2010 | NA | REQ | NA | NA | REQ | NA | Check 9.4.1.4 | Check 9.4.1.5 | Check 9.4.1.6 | NA
Religious Facility - Fellowship hall | 0.55 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | NA | ADD2 | ADD2 | NA | NA | Religious Buildings - Fellowship Hall | 0.64 | 4 | REQ | REQ | NA | REQ | NA | Check 9.4.1.4 | Check 9.4.1.5 | Check 9.4.1.6 | NA
Religious Facility - Worship/pulpit/choir area | 1.53 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | NA | ADD2 | ADD2 | NA | NA | Religious Buildings - Worship Pulpit, Choir | 1.53 | 4 | REQ | REQ | NA | REQ | NA | Check 9.4.1.4 | Check 9.4.1.5 | Check 9.4.1.6 | NA
Restroom - All other restrooms | 0.85 | 8 | NA | NA | NA | NA | REQ | REQ | NA | REQ | NA | NA | NA | Restrooms | 0.98 | 8 | REQ | NA | REQ | NA | NA | Check 9.4.1.4 | Check 9.4.1.5 | Check 9.4.1.6 | NA
Restroom - Facility for the visually impaired nd not used primarily by the staff | 0.96 | 8 | NA | NA | NA | NA | REQ | REQ | NA | REQ | NA | NA | NA |  | Not 2010 | NA | REQ | NA | NA | REQ | NA | Check 9.4.1.4 | Check 9.4.1.5 | Check 9.4.1.6 | NA
Retail Facilities - Dressing/fitting room | 0.5 | 8 | REQ | ADD1 | ADD1 | REQ | NA | REQ | NA | REQ | NA | NA | NA | Retail - Dressing/Fitting Room | 0.87 | 8 | REQ | REQ | REQ | NA | NA | Check 9.4.1.4 | Check 9.4.1.5 | Check 9.4.1.6 | NA
Retail Facilities - Mall concourse | 0.9 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | NA | ADD2 | ADD2 | NA | Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage | Retail - Mall Concourse | 1.1 | 4 | REQ | NA | NA | REQ | NA | Check 9.4.1.4 | Check 9.4.1.5 | Check 9.4.1.6 | Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage
Sales Area | 1.22 | 6 | REQ | ADD1 | ADD1 | REQ | NA | REQ | NA | ADD2 | ADD2 | NA | Retail Sales Area | Retail - Sales Area | 1.68 | 6 | REQ | REQ | NA | REQ | NA | Check 9.4.1.4 | Check 9.4.1.5 | Check 9.4.1.6 | Retail Sales Area
Seating Area, General | 0.42 | 4 | REQ | ADD1 | ADD1 | NA | REQ | REQ | NA | ADD2 | ADD2 | NA | NA |  | Not 2010 | NA | REQ | NA | NA | REQ | NA | Check 9.4.1.4 | Check 9.4.1.5 | Check 9.4.1.6 | NA
Sports Arena - Ring Sports Area | 2.47 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | NA | ADD2 | ADD2 | NA | NA | Sports Arena - Ring Sports Area | 2.68 | 4 | REQ | REQ | NA | REQ | NA | Check 9.4.1.4 | Check 9.4.1.5 | Check 9.4.1.6 | NA
Sports Arena Playing Area - Class I facility | 2.47 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | NA | ADD2 | ADD2 | NA | NA | Sports Arena - Court Sports Area - Class 1 | 3.01 | 4 | REQ | REQ | NA | REQ | NA | Check 9.4.1.4 | Check 9.4.1.5 | Check 9.4.1.6 | NA
Sports Arena Playing Area - Class II facility | 1.96 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | NA | ADD2 | ADD2 | NA | NA | Sports Arena - Court Sports Area - Class 2 | 1.92 | 4 | REQ | REQ | NA | REQ | NA | Check 9.4.1.4 | Check 9.4.1.5 | Check 9.4.1.6 | NA
Sports Arena Playing Area - Class III facility | 1.7 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | NA | ADD2 | ADD2 | NA | NA | Sports Arena - Court Sports Area - Class 3 | 1.2 | 4 | REQ | REQ | NA | REQ | NA | Check 9.4.1.4 | Check 9.4.1.5 | Check 9.4.1.6 | NA
Sports Arena Playing Area - Class IV facility | 1.13 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | NA | ADD2 | ADD2 | NA | NA | Sports Arena - Court Sports Area - Class 4 | 0.72 | 4 | REQ | REQ | NA | REQ | NA | Check 9.4.1.4 | Check 9.4.1.5 | Check 9.4.1.6 | NA
Stairwell | 0.58 | 10 | NA | NA | NA | REQ | REQ | REQ | REQ | ADD2 | ADD2 | NA | Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage | Stairway | 0.69 | 10 | REQ | NA | NA | REQ | NA | Check 9.4.1.4 | Check 9.4.1.5 | Check 9.4.1.6 | Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage
Storage Room - All other storage rooms | 0.46 | 6 | REQ | ADD1 | ADD1 | NA | REQ | REQ | REQ | ADD2 | ADD2 | NA | NA | Storage | 0.63 | 6 | REQ | NA | REQ | NA | NA | Check 9.4.1.4 | Check 9.4.1.5 | Check 9.4.1.6 | NA
Storage Room <50 ft2 | 0.97 | 6 | REQ | NA | NA | NA | NA | NA | NA | ADD2 | ADD2 | NA | NA | Storage | 0.63 | 6 | REQ | NA | REQ | NA | NA | Check 9.4.1.4 | Check 9.4.1.5 | Check 9.4.1.6 | NA
Storage Room >=50 ft2 and <1000 ft2 | 0.46 | 6 | REQ | ADD1 | ADD1 | NA | REQ | REQ | NA | REQ | NA | NA | NA | Storage | 0.63 | 6 | REQ | NA | REQ | NA | NA | Check 9.4.1.4 | Check 9.4.1.5 | Check 9.4.1.6 | NA
Transportation Facility - Airport concourse | 0.31 | 4 | REQ | ADD1 | ADD1 | NA | REQ | REQ | NA | ADD2 | ADD2 | NA | NA | Transportation - Airport Concourse | 0.36 | 4 | REQ | NA | NA | REQ | NA | Check 9.4.1.4 | Check 9.4.1.5 | Check 9.4.1.6 | NA
Transportation Facility - Baggage/carousel area | 0.45 | 4 | REQ | ADD1 | ADD1 | NA | REQ | REQ | NA | ADD2 | ADD2 | NA | NA | Transportation - Air/Train/Bus Baggage Area | 0.76 | 4 | REQ | REQ | NA | REQ | NA | Check 9.4.1.4 | Check 9.4.1.5 | Check 9.4.1.6 | NA
Transportation Facility - Terminal ticket counter | 0.62 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | NA | ADD2 | ADD2 | NA | NA | Transportation - Terminal - Ticket Counter | 1.08 | 4 | REQ | REQ | NA | REQ | NA | Check 9.4.1.4 | Check 9.4.1.5 | Check 9.4.1.6 | NA
Vehicular Maintenance Area | 0.56 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | NA | ADD2 | ADD2 | NA | NA | Automotive - Service/Repair | 0.67 | 4 | REQ | REQ | NA | REQ | NA | Check 9.4.1.4 | Check 9.4.1.5 | Check 9.4.1.6 | NA
Warehouse Storage - Medium to bulky, palletized items | 0.35 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | REQ | ADD2 | ADD2 | NA | NA | Warehouse - Medium/Bulky Material Storage | 0.58 | 4 | REQ | REQ | NA | REQ | NA | Check 9.4.1.4 | Check 9.4.1.5 | Check 9.4.1.6 | NA
Warehouse Storage - Smaller, hand-carried items | 0.69 | 6 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | REQ | ADD2 | ADD2 | NA | NA | Warehouse - Fine Material Storage | 0.95 | 6 | REQ | REQ | NA | REQ | NA | Check 9.4.1.4 | Check 9.4.1.5 | Check 9.4.1.6 | NA
Workshop | 1.14 | 6 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | NA | ADD2 | ADD2 | NA | NA | Workshop | 1.59 | 6 | REQ | REQ | NA | REQ | NA | Check 9.4.1.4 | Check 9.4.1.5 | Check 9.4.1.6 | NA
Table 9.6.1 Lighting Power Density Allowances Using the Space-by-Space Method and Minimum Control Requirements Using Either Method
|  | Informative Note: This table is divided into two sections; this first section covers space types that can be commonly found in multiple building types. The second part of this table covers space types that are typically found in a single building type. |  |  | The control functions below shall be implemented in accordance with the descriptions found in the referenced paragraphs within
Section 9.4.1.1. For each space type:
(1) All REQs shall be implemented.
(2) At least one ADD1 (when present) shall be implemented.
(3) At least one ADD2 (when present) shall be implemented.
0.40 + 0.02/ft total height |  |  |  |  | Local Control (See Section 9.4.1.1[a]) | Restricted to Manual ON (See Section 9.4.1.1[b]) | Restricted to Partial Automatic ON (See Section 9.4.1.1[c]) | Bilevel Lighting Control (See Section 9.4.1.1[d]) | Automatic Daylight Responsive Controls for Sidelighting (See Section 9.4.1.1[e]6) | Automatic Daylight Responsive Controls for Toplighting (See Section 9.4.1.1[f]6) | Automatic Partial OFF (See Section 9.4.1.1[g] [Full Off complies]) |  |  | Automatic Full OFF (See Section 9.4.1.1[h]) | Scheduled Shutoff (See Section 9.4.1.1[i])
|  | Space Types1 | LPD Allowances, W/ft2 | RCR Threshold | a | b | c | d | e | f | g |  |  | h | i | 9.6.2c
Atrium <20 ft in height | Atrium | <20 ft in height | 0.03 | NA | REQ | ADD1 | ADD1 |  | REQ | REQ |  |  |  | ADD2 | ADD2 | Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage
Atrium >=20 ft and <=40 ft in height | Atrium | >=20 ft and <=40 ft in height | 0.03 | NA | REQ | ADD1 | ADD1 | REQ | REQ | REQ |  |  |  | ADD2 | ADD2 | Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage
Atrium >40 ft in height | Atrium | >40 ft in height | 0.02 | NA | REQ | ADD1 | ADD1 | REQ | REQ | REQ |  |  |  | ADD2 | ADD2 | Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage
Audience Seating Area in all other audience areas | Audience Seating Area in | all other audience areas | 0.43 | 4 | REQ | ADD1 | ADD1 |  | REQ | REQ |  |  |  | ADD2 | ADD2 | NA
Audience Seating Area in Auditorium | Audience Seating Area in | Auditorium | 0.63 | 6 | REQ | ADD1 | ADD1 | REQ | REQ | REQ |  |  |  | ADD2 | ADD2 | NA
Audience Seating Area in Convention center | Audience Seating Area in | Convention center | 0.82 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ |  |  |  | ADD2 | ADD2 | NA
Audience Seating Area in Gymnasium | Audience Seating Area in | Gymnasium | 0.65 | 6 | REQ | ADD1 | ADD1 | REQ | REQ | REQ |  |  |  | ADD2 | ADD2 | NA
Audience Seating Area in Motion picture theater | Audience Seating Area in | Motion picture theater | 1.14 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ |  |  |  | ADD2 | ADD2 | NA
Audience Seating Area in Penitentiary | Audience Seating Area in | Penitentiary | 0.28 | 4 | REQ | ADD1 | ADD1 |  | REQ | REQ |  |  |  | ADD2 | ADD2 | NA
Audience Seating Area in Performing arts theater | Audience Seating Area in | Performing arts theater | 2.03 | 8 | REQ | ADD1 | ADD1 | REQ | REQ | REQ |  |  |  | ADD2 | ADD2 | NA
Audience Seating Area in Religious facility | Audience Seating Area in | Religious facility | 1.53 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ |  |  |  | ADD2 | ADD2 | NA
Audience Seating Area in Sports arena | Audience Seating Area in | Sports arena | 0.43 | 4 | REQ | ADD1 | ADD1 |  | REQ | REQ |  |  |  | ADD2 | ADD2 | NA
Banking Activity Area - Bank/Office | Banking Activity Area - | Bank/Office | 0.86 | 6 | REQ | ADD1 | ADD1 | REQ | REQ | REQ |  |  |  | ADD2 | ADD2 | NA
Chapel for the Visually Impaired (used primarily by residents) | Chapel | for the Visually Impaired (used primarily by residents) | 1.06 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ |  |  |  | ADD2 | ADD2 | NA
Classroom - Laboratory in or as a classroom |  | Classroom - Laboratory in or as a classroom | 1.2 | 6 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | REQ |  |  | ADD2 | ADD2 | Conference Room, Meeting Room, Classroom (Lecture/Training)
Classroom/ Lecture Hall/ Training Room in a Penitentiary |  | Classroom/ Lecture Hall/ Training Room in a Penitentiary | 1.34 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ |  |  |  | REQ |  | Conference Room, Meeting Room, Classroom (Lecture/Training)
Classrooms/ lecture halls/ training rooms in all other areas |  | Classrooms/ lecture halls/ training rooms in all other areas | 0.92 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ |  |  |  | REQ |  | Conference Room, Meeting Room, Classroom (Lecture/Training)
Computer Room |  | Computer Room | 1.33 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ |  |  |  | ADD2 | ADD2 | NA
Conference/ Meeting/ Multipurpose Room |  | Conference/ Meeting/ Multipurpose Room | 1.07 | 6 | REQ | ADD1 | ADD1 | REQ | REQ | REQ |  |  |  | REQ |  | Conference Room, Meeting Room, Classroom (Lecture/Training)
Confinement Cells |  | Confinement Cells | 0.81 | 6 | REQ | ADD1 | ADD1 | REQ | REQ | REQ |  |  |  | ADD2 | ADD2 | NA
Convention Center - Exhibit Space |  | Convention Center - Exhibit Space | 0.88 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ |  |  |  | ADD2 | ADD2 | NA
Copy/Print Room |  | Copy/Print Room | 0.56 | 6 | REQ | ADD1 | ADD1 | REQ | REQ | REQ |  |  |  | REQ |  | NA
Corridor Facility for the visually impaired (and not used primarily by the staff) | Corridor | Facility for the visually impaired (and not used primarily by the staff) | 0.92 | width <8 ft | REQ |  |  |  | REQ | REQ | REQ |  |  | ADD2 | ADD2 | Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage
Corridor in all other other areas | Corridor in | all other other areas | 0.66 | width <8 ft | REQ |  |  |  | REQ | REQ | REQ |  |  | ADD2 | ADD2 | Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage
Corridor in a Hospital | Corridor in a | Hospital | 0.92 | width <8 ft | REQ |  |  |  | REQ | REQ | REQ |  |  | ADD2 | ADD2 | Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage
Corridor in a Manufacturing facility | Corridor in a | Manufacturing facility | 0.29 | width <8 ft | REQ |  |  |  | REQ | REQ |  |  |  | ADD2 | ADD2 | Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage
Courtroom |  | Courtroom | 1.39 | 6 | REQ | ADD1 | ADD1 | REQ | REQ | REQ |  |  |  | ADD2 | ADD2 | NA
Dining Area in all other dining areas | Dining Area in | all other dining areas | 0.63 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ |  |  |  | ADD2 | ADD2 | Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage
Dining Area in a Bar/lounge or leisure dining | Dining Area in a | Bar/lounge or leisure dining | 0.93 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ |  |  |  | ADD2 | ADD2 | Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage
Dining Area in a Cafeteria or fast food dining | Dining Area in a | Cafeteria or fast food dining | 0.63 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ |  |  |  | ADD2 | ADD2 | Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage
Dining Area in a Facility for the visually impaired (and not u(and not used primarily by staff)sed primarily by the staff) | Dining Area in a | Facility for the visually impaired (and not u(and not used primarily by staff)sed primarily by the staff) | 2 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ |  |  |  | ADD2 | ADD2 | Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage
Dining Area in a Family dining area | Dining Area in a | Family dining area | 0.71 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ |  |  |  | ADD2 | ADD2 | Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage
Dining Area in a Penitentiary | Dining Area in a | Penitentiary | 0.96 | 6 | REQ | ADD1 | ADD1 | REQ | REQ | REQ |  |  |  | ADD2 | ADD2 | Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage
Dormitory - Living Quarters |  | Dormitory - Living Quarters | 0.54 | 8 | REQ | [10 empty] | NA
Electrical/Mechanical Room |  | Electrical/Mechanical Room | 0.43 | 6 | REQ |  |  |  | REQ | REQ | [5 empty] | NA
Emergency Vehicle Garage |  | Emergency Vehicle Garage | 0.41 | 4 | REQ | ADD1 | ADD1 |  | REQ | REQ |  |  |  | ADD2 | ADD2 | NA
Fire Station - Sleeping Quarters |  | Fire Station - Sleeping Quarters | 0.2 | 6 | REQ | [10 empty] | NA
Food Preparation Area |  | Food Preparation Area | 1.06 | 6 | REQ | ADD1 | ADD1 | REQ | REQ | REQ |  |  |  | ADD2 | ADD2 | NA
Guest Room |  | Guest Room | 0.77 | 6 | See Section 9.4.1.3(b). | See Section 9.4.1.3(b). | See Section 9.4.1.3(b). | See Section 9.4.1.3(b). | See Section 9.4.1.3(b). | See Section 9.4.1.3(b). | See Section 9.4.1.3(b). |  |  | See Section 9.4.1.3(b). | See Section 9.4.1.3(b). | NA
Gymnasium/Fitness Center Exercise area | Gymnasium/Fitness Center | Exercise area | 0.5 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ |  |  |  | ADD2 | ADD2 | Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage
Gymnasium/Fitness Center Playing area | Gymnasium/Fitness Center | Playing area | 0.82 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ |  |  |  | ADD2 | ADD2 | Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage
Healthcare Facility - Exam/treatment room | Healthcare Facility - | Exam/treatment room | 1.68 | 8 | REQ |  |  | REQ | REQ | REQ |  |  |  | ADD2 | ADD2 | NA
Healthcare Facility - Imaging room | Healthcare Facility - | Imaging room | 1.06 | 6 | REQ |  |  | REQ | [5 empty] | ADD2 | ADD2 | NA
Healthcare Facility - Medical supply room | Healthcare Facility - | Medical supply room | 0.54 | 6 | See “Storage Room” | See “Storage Room” | See “Storage Room” | See “Storage Room” | See “Storage Room” | See “Storage Room” | See “Storage Room” |  |  | See “Storage Room” | See “Storage Room” | NA
Healthcare Facility - Nurse’s station | Healthcare Facility - | Nurse’s station | 0.81 | 6 | REQ |  |  | REQ | REQ | REQ |  |  |  | ADD2 | ADD2 | NA
Healthcare Facility - Nursery | Healthcare Facility - | Nursery | 1 | 6 | REQ |  |  | REQ | REQ | REQ |  |  |  | ADD2 | ADD2 | NA
Healthcare Facility - Operating room | Healthcare Facility - | Operating room | 2.17 | 6 | REQ |  |  | REQ | [5 empty] | ADD2 | ADD2 | NA
Healthcare Facility - Patient room | Healthcare Facility - | Patient room | 0.62 | 6 | REQ |  |  | REQ | REQ | REQ |  |  |  | ADD2 | ADD2 | NA
Healthcare Facility - Physical therapy room | Healthcare Facility - | Physical therapy room | 0.84 | 6 | REQ |  |  | REQ | REQ | REQ |  |  |  | ADD2 | ADD2 | NA
Healthcare Facility - Recovery room | Healthcare Facility - | Recovery room | 1.03 | 6 | REQ |  |  | REQ | REQ | REQ |  |  |  | ADD2 | ADD2 | NA
Laboratories - not in or as a classroom |  | Laboratories - not in or as a classroom | 1.45 | 6 | REQ | ADD1 | ADD1 | REQ | REQ | REQ |  |  |  | ADD2 | ADD2 | NA
Laundry/Washing Area |  | Laundry/Washing Area | 0.43 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ |  |  |  | ADD2 | ADD2 | NA
Library - Reading area | Library - | Reading area | 0.82 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ |  |  |  | ADD2 | ADD2 | NA
Library - Stacks | Library - | Stacks | 1.2 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | REQ |  |  | ADD2 | ADD2 | NA
Loading Dock, Interior |  | Loading Dock, Interior | 0.58 | 6 | REQ | ADD1 | ADD1 |  | REQ | REQ |  |  |  | ADD2 | ADD2 | NA
Lobby - All other lobbies | Lobby - | All other lobbies | 1 | 4 | REQ |  |  |  | REQ | REQ | REQ |  |  | ADD2 | ADD2 | Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage
Lobby - Elevator lobby | Lobby - | Elevator lobby | 0.69 | 6 | REQ |  |  |  | REQ | REQ |  |  |  | ADD2 | ADD2 | Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage
Lobby Facility for the visually impaired (and not used primarily by the staff) | Lobby | Facility for the visually impaired (and not used primarily by the staff) | 2.03 | 4 | REQ |  |  |  | REQ | REQ | REQ |  |  | ADD2 | ADD2 | Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage
Lobby in a Hotel | Lobby in a | Hotel | 1.06 | 4 | REQ |  |  |  | REQ | REQ |  |  |  | ADD2 | ADD2 | Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage
Lobby in a Motion picture theater | Lobby in a | Motion picture theater | 0.45 | 4 | REQ |  |  |  | REQ | REQ |  |  |  | ADD2 | ADD2 | Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage
Lobby in a Performing arts theater | Lobby in a | Performing arts theater | 1.7 | 6 | REQ |  |  |  | REQ | REQ | REQ |  |  | ADD2 | ADD2 | Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage
Locker Room |  | Locker Room | 0.48 | 6 | REQ | ADD1 | ADD1 | REQ | REQ | REQ |  |  |  | ADD2 | ADD2 | NA
Lounge/Breakroom in a Healthcare facility |  | Lounge/Breakroom in a Healthcare facility | 0.78 | 6 | REQ | ADD1 | ADD1 | REQ | REQ | REQ |  |  |  | ADD2 | ADD2 | NA
Lounges/breakrooms - All other |  | Lounges/breakrooms - All other | 0.62 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ |  |  |  | ADD2 | ADD2 | NA
Manufacturing Facility - (<25 ft floor-to-ceiling height) | Manufacturing Facility - | (<25 ft floor-to-ceiling height) | 0.96 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ |  |  |  | ADD2 | ADD2 | NA
Manufacturing Facility - (>50 ft floor-to-ceiling height) | Manufacturing Facility - | (>50 ft floor-to-ceiling height) | 0.75 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ |  |  |  | ADD2 | ADD2 | NA
Manufacturing Facility - (25 to 50 ft floor-to-ceiling height) | Manufacturing Facility - | (25 to 50 ft floor-to-ceiling height) | 1.05 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ |  |  |  | ADD2 | ADD2 | NA
Manufacturing Facility - Detailed manufacturing area | Manufacturing Facility - | Detailed manufacturing area | 0.93 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ |  |  |  | ADD2 | ADD2 | NA
Manufacturing Facility - Equipment room | Manufacturing Facility - | Equipment room | 0.65 | 6 | REQ | ADD1 | ADD1 | REQ | REQ | REQ |  |  |  | ADD2 | ADD2 | NA
Manufacturing Facility - Extra high bay area | Manufacturing Facility - | Extra high bay area | 1.05 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ |  |  |  | ADD2 | ADD2 | NA
Manufacturing Facility - High bay area | Manufacturing Facility - | High bay area | 0.75 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ |  |  |  | ADD2 | ADD2 | NA
Manufacturing Facility - Low bay area | Manufacturing Facility - | Low bay area | 0.96 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ |  |  |  | ADD2 | ADD2 | NA
Museum - General exhibition area | Museum - | General exhibition area | 1.05 | 6 | REQ | ADD1 | ADD1 | REQ | REQ | REQ |  |  |  | ADD2 | ADD2 | NA
Museum - Restoration room | Museum - | Restoration room | 0.85 | 6 | REQ | ADD1 | ADD1 | REQ | REQ | REQ |  |  |  | ADD2 | ADD2 | NA
Office - Enclosed and <=250 ft | Office - | Enclosed and <=250 ft | 0.93 | 8 | REQ | ADD1 | ADD1 | REQ | REQ | REQ |  |  |  | REQ |  | Private Office
Office - Enclosed and >250 ft | Office - | Enclosed and >250 ft | 0.93 | 8 | REQ | ADD1 | ADD1 | REQ | REQ | REQ |  |  |  | ADD2 | ADD2 | Private Office
Office - Open plan | Office - | Open plan | 0.81 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ |  |  |  | ADD2 | ADD2 | Open Office
Parking Area - Garage |  | Parking Area - Garage | 0.14 | 4 | See Section 9.4.1.2. | See Section 9.4.1.2. | See Section 9.4.1.2. | See Section 9.4.1.2. | See Section 9.4.1.2. | See Section 9.4.1.2. | See Section 9.4.1.2. |  |  | See Section 9.4.1.2. | See Section 9.4.1.2. | Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage
Performing Arts Theater - Dressing Room |  | Performing Arts Theater - Dressing Room | 0.36 | 6 | REQ | ADD1 | ADD1 | REQ | REQ | REQ |  |  |  | REQ |  | NA
Pharmacy Area |  | Pharmacy Area | 1.34 | 6 | REQ | ADD1 | ADD1 | REQ | REQ | REQ |  |  |  | ADD2 | ADD2 | NA
Post Office - Sorting Area |  | Post Office - Sorting Area | 0.68 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | REQ |  |  | ADD2 | ADD2 | NA
Recreation Room/ Common Living Room (and not used primarily by staff) for the Visually Impaired (used primarily by residents) | Recreation Room/ Common Living Room (and not used primarily by staff) | for the Visually Impaired (used primarily by residents) | 1.8 | 6 | REQ | ADD1 | ADD1 | REQ | REQ | REQ |  |  |  | ADD2 | ADD2 | NA
Religious Facility - Fellowship hall | Religious Facility - | Fellowship hall | 0.55 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ |  |  |  | ADD2 | ADD2 | NA
Religious Facility - Worship/pulpit/choir area | Religious Facility - | Worship/pulpit/choir area | 1.53 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ |  |  |  | ADD2 | ADD2 | NA
Restroom in a facility for the visually impaired (and not used primarily by the staff)3 |  | Restroom in a facility for the visually impaired (and not used primarily by the staff)3 | 0.96 | 8 |  |  |  |  | REQ | REQ |  |  |  | REQ |  | NA
Restrooms - All other |  | Restrooms - All other | 0.85 | 8 |  |  |  |  | REQ | REQ |  |  |  | REQ |  | NA
Retail Facilities - Dressing/fitting room | Retail Facilities - | Dressing/fitting room | 0.5 | 8 | REQ | ADD1 | ADD1 | REQ |  | REQ |  |  |  | REQ |  | NA
Retail Facilities - Mall concourse | Retail Facilities - | Mall concourse | 0.9 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ |  |  |  | ADD2 | ADD2 | Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage
Sales Area |  | Sales Area | 1.22 | 6 | REQ | ADD1 | ADD1 | REQ |  | REQ |  |  |  | ADD2 | ADD2 | Retail Sales Area
Seating Area, General |  | Seating Area, General | 0.42 | 4 | REQ | ADD1 | ADD1 |  | REQ | REQ |  |  |  | ADD2 | ADD2 | NA
Sports Arena - Playing Area Class I facility | Sports Arena - Playing Area | Class I facility | 2.47 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ |  |  |  | ADD2 | ADD2 | NA
Sports Arena - Playing Area Class II facility | Sports Arena - Playing Area | Class II facility | 1.96 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ |  |  |  | ADD2 | ADD2 | NA
Sports Arena - Playing Area Class III facility | Sports Arena - Playing Area | Class III facility | 1.7 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ |  |  |  | ADD2 | ADD2 | NA
Sports Arena - Playing Area Class IV facility | Sports Arena - Playing Area | Class IV facility | 1.13 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ |  |  |  | ADD2 | ADD2 | NA
Stairwell |  | Stairwell | 0.58 | 10 |  |  |  | REQ | REQ | REQ | REQ |  |  | ADD2 | ADD2 | Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage
Storage Room <50 ft2 | Storage Room | <50 ft2 | 0.97 | 6 | REQ | [8 empty] | ADD2 | ADD2 | NA
Storage Room >=50 ft2 and <=1000 ft2 | Storage Room | >=50 ft2 and <=1000 ft2 | 0.46 | 6 | REQ | ADD1 | ADD1 |  | REQ | REQ |  |  |  | REQ |  | NA
Storage Room All other storage rooms | Storage Room | All other storage rooms | 0.46 | 6 | REQ | ADD1 | ADD1 |  | REQ | REQ | REQ |  |  | ADD2 | ADD2 | NA
Transportation Facility - Airport concourse | Transportation Facility - | Airport concourse | 0.31 | 4 | REQ | ADD1 | ADD1 |  | REQ | REQ |  |  |  | ADD2 | ADD2 | NA
Transportation Facility - Baggage/carousel area | Transportation Facility - | Baggage/carousel area | 0.45 | 4 | REQ | ADD1 | ADD1 |  | REQ | REQ |  |  |  | ADD2 | ADD2 | NA
Transportation Facility - Ticket counter | Transportation Facility - | Ticket counter | 0.62 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ |  |  |  | ADD2 | ADD2 | NA
Vehicular Maintenance Area |  | Vehicular Maintenance Area | 0.56 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ |  |  |  | ADD2 | ADD2 | NA
Warehouse - Storage Area Medium to bulky, palletized items | Warehouse - Storage Area | Medium to bulky, palletized items | 0.35 | 4 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | REQ |  |  | ADD2 | ADD2 | NA
Warehouse - Storage Area Smaller, hand-carried items | Warehouse - Storage Area | Smaller, hand-carried items | 0.69 | 6 | REQ | ADD1 | ADD1 | REQ | REQ | REQ | REQ |  |  | ADD2 | ADD2 | NA
Workshop |  | Workshop | 1.14 | 6 | REQ | ADD1 | ADD1 | REQ | REQ | REQ |  |  |  | ADD2 | ADD2 | NA
1. In cases where both a common space type and a building area specific space type are listed, the building area specific space type shall apply
2. In corridors, the extra lighting power density allowance is permitted when the width of the corridor is less than 8 ft and is not based on the RCR.
3. A “Facility for the Visually Impaired” is a facility that can be documented as being designed to comply with the light levels in ANSI/IES RP-28 and is licensed or will be licensed by local/state authorities for either senior long-term care, adult daycare, senior support and/or people with special visual needs.
4. For accent lighting, see Section 9.6.2(b).
5. Sometimes referred to as a “Picking Area.”
6. Automatic daylight responsive controls are mandatory only if the requirements of the specified sections are present.
7. An additional 0.52 W/ft2 shall be allowed, provided that the additional lighting is controlled separately from the base allowance of 0.43 W/ft2. The additional 0.52 W/ft2 allowance shall not be used for any other purpose.
8. Class of play as defined by IES RP-6.
2010
Space Types (SSpaceType3) |  |  | LPD | RCR | 9.4.1.1 Automatic Lighting Shutoff | 9.4.1.2 Space Control (a) Bi-Level | 9.4.1.2 Space Control (b) Occ | 9.4.1.2 Space Control (c) | 9.4.1.3 Parking Garage Lighting Control | 9.4.1.4 Automatic Daylighting Controls for Primary Sidelighted Areas | 9.4.1.5 Automatic Daylighting Controls for Toplighting |  |  | 9.4.1.6 Additional Control
Atrium - First 40 ft in height |  |  | 0.03 | na | REQ | N/A | N/A | REQ | N/A | - | - |  |  | - | - | Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage
Atrium >40 ft in height |  |  | 0.02 | na | REQ | N/A | N/A | REQ | N/A | - | - |  |  | - | - | Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage
Audience/Seating Area - Auditorium |  |  | 0.79 | 6 | REQ | REQ | N/A | REQ | N/A | - | - |  |  | - | - | NA
Audience/Seating Area - Motion Picture Theater |  |  | 1.14 | 4 | REQ | REQ | N/A | REQ | N/A | - | - |  |  | - | - | NA
Audience/Seating Area - Performing Arts Theater |  |  | 2.43 | 8 | REQ | REQ | N/A | REQ | N/A | - | - |  |  | - | - | NA
Classroom/Lecture/Training |  |  | 1.24 | 4 | REQ | REQ | REQ | N/A | N/A | - | - |  |  | - | - | Conference Room, Meeting Room, Classroom (Lecture/Training)
Conference/Meeting/Multipurpose |  |  | 1.23 | 6 | REQ | REQ | REQ | N/A | N/A | - | - |  |  | - | - | Conference Room, Meeting Room, Classroom (Lecture/Training)
Corridor/Transition |  |  | 0.66 | 8' wide | REQ | N/A | N/A | REQ | N/A | - | - |  |  | - | - | Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage
Dining Area |  |  | 0.65 | 4 | REQ | REQ | N/A | REQ | N/A | - | - |  |  | - | - | Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage
Dining Area - Bar Lounge/Leisure Dining |  |  | 1.31 | 4 | REQ | REQ | N/A | REQ | N/A | - | - |  |  | - | - | Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage
Dining Area - Family Dining |  |  | 0.89 | 4 | REQ | REQ | N/A | REQ | N/A | - | - |  |  | - | - | Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage
Dressing/Fitting Room - Performing Arts Theater |  |  | 0.4 | 6 | REQ | REQ | REQ | N/A | N/A | - | - |  |  | - | - | NA
Electrical/Mechanical Room |  |  | 0.95 | 6 | REQ | N/A | N/A | REQ | N/A | - | - |  |  | - | - | NA
Food Preperation |  |  | 0.99 | 6 | REQ | REQ | N/A | REQ | N/A | - | - |  |  | - | - | NA
Laboratory - Classroom |  |  | 1.28 | 6 | REQ | REQ | REQ | N/A | N/A | - | - |  |  | - | - | Conference Room, Meeting Room, Classroom (Lecture/Training)
Laboratory - Research |  |  | 1.81 | 6 | REQ | REQ | N/A | REQ | N/A | - | - |  |  | - | - | NA
Lobby |  |  | 0.9 | 4 | REQ | N/A | N/A | REQ | N/A | - | - |  |  | - | - | Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage
Lobby - Elevator |  |  | 0.64 | 6 | REQ | N/A | N/A | REQ | N/A | - | - |  |  | - | - | Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage
Lobby - Motion Picture Theater |  |  | 0.52 | 4 | REQ | N/A | N/A | REQ | N/A | - | - |  |  | - | - | Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage
Lobby - Performing Arts Theater |  |  | 2 | 6 | REQ | N/A | N/A | REQ | N/A | - | - |  |  | - | - | Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage
Locker Room |  |  | 0.75 | 6 | REQ | REQ | REQ | N/A | N/A | - | - |  |  | - | - | NA
Lounge/Recreation |  |  | 0.73 | 4 | REQ | REQ | REQ | N/A | N/A | - | - |  |  | - | - | NA
Office-Enclosed |  |  | 1.11 | 8 | REQ | REQ | REQ | N/A | N/A | - | - |  |  | - | - | Private Office
Office-Open |  |  | 0.98 | 4 | REQ | REQ | N/A | REQ | N/A | - | - |  |  | - | - | Open Office
Restrooms |  |  | 0.98 | 8 | REQ | N/A | REQ | N/A | N/A | - | - |  |  | - | - | NA
Sales Area |  |  | 1.68 | 6 | REQ | REQ | N/A | REQ | N/A | - | - |  |  | - | - | Retail Sales Area
Stairway |  |  | 0.69 | 10 | REQ | N/A | N/A | REQ | N/A | - | - |  |  | - | - | Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage
Storage |  |  | 0.63 | 6 | REQ | N/A | REQ | N/A | N/A | - | - |  |  | - | - | NA
Workshop |  |  | 1.59 | 6 | REQ | REQ | N/A | REQ | N/A | - | - |  |  | - | - | NA
Automotive - Service/Repair |  |  | 0.67 | 4 | REQ | REQ | N/A | REQ | N/A | - | - |  |  | - | - | NA
Bank/Office - Banking Activity Area |  |  | 1.38 | 6 | REQ | REQ | N/A | REQ | N/A | - | - |  |  | - | - | NA
Convention Center - Audience Seating |  |  | 0.82 | 4 | REQ | REQ | N/A | REQ | N/A | - | - |  |  | - | - | NA
Convention Center - Exhibit Space |  |  | 1.45 | 4 | REQ | REQ | N/A | REQ | N/A | - | - |  |  | - | - | NA
Courthouse/Police Station/Penitentiary - Confinement Cells |  |  | 1.1 | 6 | REQ | REQ | N/A | REQ | N/A | - | - |  |  | - | - | NA
Courthouse/Police Station/Penitentiary - Courtroom |  |  | 1.72 | 6 | REQ | REQ | N/A | REQ | N/A | - | - |  |  | - | - | NA
Courthouse/Police Station/Penitentiary - Judges' Chambers |  |  | 1.17 | 8 | REQ | REQ | N/A | REQ | N/A | - | - |  |  | - | - | NA
Courthouse/Police Station/Penitentiary - Penitentiary Audience Seating |  |  | 0.43 | 4 | REQ | REQ | N/A | REQ | N/A | - | - |  |  | - | - | NA
Courthouse/Police Station/Penitentiary - Penitentiary Dining |  |  | 1.07 | 6 | REQ | REQ | N/A | REQ | N/A | - | - |  |  | - | - | NA
Courthouse/Police Station/Penitentiary - Pentitentiary Classroom |  |  | 1.34 | 4 | REQ | REQ | N/A | REQ | N/A | - | - |  |  | - | - | NA
Dormitory - Living Quarters |  |  | 0.38 | 8 | REQ | REQ | N/A | REQ | N/A | - | - |  |  | - | - | NA
Fire Stations - Engine Room |  |  | 0.56 | 4 | REQ | REQ | N/A | REQ | N/A | - | - |  |  | - | - | NA
Fire Stations - Sleeping Quarters |  |  | 0.25 | 6 | REQ | REQ | N/A | REQ | N/A | - | - |  |  | - | - | NA
Gymnasium/Fitness Center - Fitness Area |  |  | 0.72 | 4 | REQ | REQ | N/A | REQ | N/A | - | - |  |  | - | - | Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage
Gymnasium/Fitness Center - Gymnasium - Audience Seating |  |  | 0.43 | 6 | REQ | REQ | N/A | REQ | N/A | - | - |  |  | - | - | Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage
Gymnasium/Fitness Center - Playing Area |  |  | 1.2 | 4 | REQ | REQ | N/A | REQ | N/A | - | - |  |  | - | - | Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage
Hospital - Corridor/Transition |  |  | 0.89 | 8' wide | REQ | N/A | N/A | REQ | N/A | - | - |  |  | - | - | NA
Hospital - Emergency |  |  | 2.26 | 6 | REQ | REQ | N/A | REQ | N/A | - | - |  |  | - | - | NA
Hospital - Exam/Treatment |  |  | 1.66 | 8 | REQ | REQ | N/A | REQ | N/A | - | - |  |  | - | - | NA
Hospital - Laundry - Washing |  |  | 0.6 | 4 | REQ | REQ | N/A | REQ | N/A | - | - |  |  | - | - | NA
Hospital - Lounge/Recreation |  |  | 1.07 | 6 | REQ | REQ | N/A | REQ | N/A | - | - |  |  | - | - | NA
Hospital - Medical Supply |  |  | 1.27 | 6 | REQ | REQ | N/A | REQ | N/A | - | - |  |  | - | - | NA
Hospital - Nursery |  |  | 0.88 | 6 | REQ | REQ | N/A | REQ | N/A | - | - |  |  | - | - | NA
Hospital - Nurses' Station |  |  | 0.87 | 6 | REQ | REQ | N/A | REQ | N/A | - | - |  |  | - | - | NA
Hospital - Operating Room |  |  | 1.89 | 6 | REQ | REQ | N/A | REQ | N/A | - | - |  |  | - | - | NA
Hospital - Patient Room |  |  | 0.62 | 6 | REQ | REQ | N/A | REQ | N/A | - | - |  |  | - | - | NA
Hospital - Pharmacy |  |  | 1.14 | 6 | REQ | REQ | N/A | REQ | N/A | - | - |  |  | - | - | NA
Hospital - Physical Therapy |  |  | 0.91 | 6 | REQ | REQ | N/A | REQ | N/A | - | - |  |  | - | - | NA
Hospital - Radiology/Imaging |  |  | 1.32 | 6 | REQ | REQ | N/A | REQ | N/A | - | - |  |  | - | - | NA
Hospital - Recovery |  |  | 1.15 | 6 | REQ | REQ | N/A | REQ | N/A | - | - |  |  | - | - | NA
Hotel/Motel - Highway Lodging Dining |  |  | 0.88 | 4 | REQ | REQ | N/A | REQ | N/A | - | - |  |  | - | - | NA
Hotel/Motel - Highway Lodging Guest Room |  |  | 0.75 | 6 | REQ | REQ | N/A | REQ | N/A | - | - |  |  | - | - | NA
Hotel/Motel - Hotel Dining |  |  | 0.82 | 4 | REQ | REQ | N/A | REQ | N/A | - | - |  |  | - | - | NA
Hotel/Motel - Hotel Guest Rooms |  |  | 1.11 | 6 | REQ | REQ | N/A | REQ | N/A | - | - |  |  | - | - | NA
Hotel/Motel - Hotel Lobby |  |  | 1.06 | 4 | REQ | N/A | N/A | REQ | N/A | - | - |  |  | - | - | NA
Library - Card File & Cataloging |  |  | 0.72 | 4 | REQ | REQ | N/A | REQ | N/A | - | - |  |  | - | - | NA
Library - Reading Area |  |  | 0.93 | 4 | REQ | REQ | N/A | REQ | N/A | - | - |  |  | - | - | NA
Library - Stacks |  |  | 1.71 | 4 | REQ | REQ | N/A | REQ | N/A | - | - |  |  | - | - | NA
Manufacturing - Corridor/Transition |  |  | 0.41 | 8' wide | REQ | N/A | N/A | REQ | N/A | - | - |  |  | - | - | NA
Manufacturing - Detailed Manufacturing |  |  | 1.29 | 4 | REQ | REQ | N/A | REQ | N/A | - | - |  |  | - | - | NA
Manufacturing - Equipment Room |  |  | 0.95 | 6 | REQ | REQ | N/A | REQ | N/A | - | - |  |  | - | - | NA
Manufacturing - Extra High Bay (≥ 50') |  |  | 1.05 | 4 | REQ | REQ | N/A | REQ | N/A | - | - |  |  | - | - | NA
Manufacturing - High Bay (≥ 25' & < 50') |  |  | 1.23 | 4 | REQ | REQ | N/A | REQ | N/A | - | - |  |  | - | - | NA
Manufacturing - Low Bay (< 25') |  |  | 1.19 | 4 | REQ | REQ | N/A | REQ | N/A | - | - |  |  | - | - | NA
Museum - General Exhibition |  |  | 1.05 | 6 | REQ | REQ | N/A | REQ | N/A | - | - |  |  | - | - | NA
Museum - Restoration |  |  | 1.02 | 6 | REQ | REQ | N/A | REQ | N/A | - | - |  |  | - | - | NA
Parking Garage - Garage Area |  |  | 0.19 | 4 | REQ | REQ | N/A | REQ | REQ | - | - |  |  | - | - | Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage
Post Office - Sorting Area |  |  | 0.94 | 4 | REQ | REQ | N/A | REQ | N/A | - | - |  |  | - | - | NA
Religious Buildings - Audience Seating |  |  | 1.53 | 4 | REQ | REQ | N/A | REQ | N/A | - | - |  |  | - | - | NA
Religious Buildings - Fellowship Hall |  |  | 0.64 | 4 | REQ | REQ | N/A | REQ | N/A | - | - |  |  | - | - | NA
Religious Buildings - Worship Pulpit, Choir |  |  | 1.53 | 4 | REQ | REQ | N/A | REQ | N/A | - | - |  |  | - | - | NA
Retail - Dressing/Fitting Room |  |  | 0.87 | 8 | REQ | REQ | REQ | N/A | N/A | - | - |  |  | - | - | NA
Retail - Mall Concourse |  |  | 1.1 | 4 | REQ | N/A | N/A | REQ | N/A | - | - |  |  | - | - | NA
Retail - Sales Area |  |  | 1.68 | 6 | REQ | REQ | N/A | REQ | N/A | - | - |  |  | - | - | Retail Sales Area
Sports Arena - Audience Seating |  |  | 0.43 | 4 | REQ | REQ | N/A | REQ | N/A | - | - |  |  | - | - | NA
Sports Arena - Court Sports Area - Class 1 |  |  | 3.01 | 4 | REQ | REQ | N/A | REQ | N/A | - | - |  |  | - | - | NA
Sports Arena - Court Sports Area - Class 2 |  |  | 1.92 | 4 | REQ | REQ | N/A | REQ | N/A | - | - |  |  | - | - | NA
Sports Arena - Court Sports Area - Class 3 |  |  | 1.2 | 4 | REQ | REQ | N/A | REQ | N/A | - | - |  |  | - | - | NA
Sports Arena - Court Sports Area - Class 4 |  |  | 0.72 | 4 | REQ | REQ | N/A | REQ | N/A | - | - |  |  | - | - | NA
Sports Arena - Ring Sports Area |  |  | 2.68 | 4 | REQ | REQ | N/A | REQ | N/A | - | - |  |  | - | - | NA
Transportation - Air/Train/Bus Baggage Area |  |  | 0.76 | 4 | REQ | REQ | N/A | REQ | N/A | - | - |  |  | - | - | NA
Transportation - Airport Concourse |  |  | 0.36 | 4 | REQ | N/A | N/A | REQ | N/A | - | - |  |  | - | - | NA
Transportation - Audience Seating |  |  | 0.54 | 4 | REQ | REQ | N/A | REQ | N/A | - | - |  |  | - | - | NA
Transportation - Terminal - Ticket Counter |  |  | 1.08 | 4 | REQ | REQ | N/A | REQ | N/A | - | - |  |  | - | - | NA
Warehouse - Fine Material Storage |  |  | 0.95 | 6 | REQ | REQ | N/A | REQ | N/A | - | - |  |  | - | - | NA
Warehouse - Medium/Bulky Material Storage |  |  | 0.58 | 4 | REQ | REQ | N/A | REQ | N/A | - | - |  |  | - | - | NA
Retail Area Choice
| 2010 |  | 2010 | 2016
Retail Area 1 | 0.6 |  | 0.6 | 0.45 |  | = the floor area for all products not listed in Retail Areas 2, 3, or 4
Retail Area 2 | 0.6 |  | 0.6 | 0.45 |  | = the floor area used for the sale of vehicles, sporting goods, and small electronics
Retail Area 3 | 1.4 |  | 1.4 | 1.05 |  | = the floor area used for the sale of furniture, clothing, cosmetics, and artwork
Retail Area 4 | 2.5 |  | 2.5 | 1.88 |  | = the floor area used for the sale of jewelry, crystal, and china
Base | 1000 |  | 1000 | 1000

## Interior Alterations
|  | Quick Links | ASHRAE/IES 90.1-2010 Lighting Compliance Documentation (v3.1)
Lighting Alterations (9.1.2 Alteration Exception)
| 90.1-2010 |  |  | 10%
| In the yellow cells below select from Drop Down one of the spaces created in Step 2 on the Room Schedule page. (Duplicate spaces MUST have the same Total Existing Wattage of the Sapce) |  | Total Existing Wattage of the Space | Max 9.1.2 exception wattage | Total square footage of the Space | Existing W/sf | Number of luminaires altered | Existing Luminaire Wattage (each) | Existing altered Wattage | Duplicate Space | Complies with 9.1.2 Exception?
[12 empty] | 0 |  | 0
1 |  |  |  | 0 | [8 empty] | 250 | 0 | No | 1 | 1 | 1 | 0
2 | [12 empty] | 250 | 0 | Yes | 1 | 1 | 1 | 0
3 | [12 empty] | 250 | 0 | Yes | 1 | 1 | 1 | 0
4 | [12 empty] | 250 | 0 | Yes | 1 | 1 | 1 | 0
5 | [12 empty] | 250 | 0 | Yes | 1 | 1 | 1 | 0
6 | [12 empty] | 250 | 0 | Yes | 1 | 1 | 1 | 0
7 | [12 empty] | 250 | 0 | Yes | 1 | 1 | 1 | 0
8 | [12 empty] | 250 | 0 | Yes | 1 | 1 | 1 | 0
9 | [12 empty] | 250 | 0 | Yes | 1 | 1 | 1 | 0
10 | [12 empty] | 250 | 0 | Yes | 1 | 1 | 1 | 0
11 | [12 empty] | 250 | 0 | Yes | 1 | 1 | 1 | 0
12 | [12 empty] | 250 | 0 | Yes | 1 | 1 | 1 | 0
13 | [12 empty] | 250 | 0 | Yes | 1 | 1 | 1 | 0
14 | [12 empty] | 250 | 0 | Yes | 1 | 1 | 1 | 0
15 | [12 empty] | 250 | 0 | Yes | 1 | 1 | 1 | 0
16 | [12 empty] | 250 | 0 | Yes | 1 | 1 | 1 | 0
17 | [12 empty] | 250 | 0 | Yes | 1 | 1 | 1 | 0
18 | [12 empty] | 250 | 0 | Yes | 1 | 1 | 1 | 0
19 | [12 empty] | 250 | 0 | Yes | 1 | 1 | 1 | 0
20 | [12 empty] | 250 | 0 | Yes | 1 | 1 | 1 | 0
21 | [12 empty] | 250 | 0 | Yes | 1 | 1 | 1 | 0
22 | [12 empty] | 250 | 0 | Yes | 1 | 1 | 1 | 0
23 | [12 empty] | 250 | 0 | Yes | 1 | 1 | 1 | 0
24 | [12 empty] | 250 | 0 | Yes | 1 | 1 | 1 | 0
25 | [12 empty] | 250 | 0 | Yes | 1 | 1 | 1 | 0
26 | [12 empty] | 250 | 0 | Yes | 1 | 1 | 1 | 0
27 | [12 empty] | 250 | 0 | Yes | 1 | 1 | 1 | 0
28 | [12 empty] | 250 | 0 | Yes | 1 | 1 | 1 | 0
29 | [12 empty] | 250 | 0 | Yes | 1 | 1 | 1 | 0
30 | [12 empty] | 250 | 0 | Yes | 1 | 1 | 1 | 0
31 | [12 empty] | 250 | 0 | Yes | 1 | 1 | 1 | 0
32 | [12 empty] | 250 | 0 | Yes | 1 | 1 | 1 | 0
33 | [12 empty] | 250 | 0 | Yes | 1 | 1 | 1 | 0
34 | [12 empty] | 250 | 0 | Yes | 1 | 1 | 1 | 0
35 | [12 empty] | 250 | 0 | Yes | 1 | 1 | 1 | 0
36 | [12 empty] | 250 | 0 | Yes | 1 | 1 | 1 | 0
37 | [12 empty] | 250 | 0 | Yes | 1 | 1 | 1 | 0
38 | [12 empty] | 250 | 0 | Yes | 1 | 1 | 1 | 0
39 | [12 empty] | 250 | 0 | Yes | 1 | 1 | 1 | 0
40 | [12 empty] | 250 | 0 | Yes | 1 | 1 | 1 | 0
41 | [12 empty] | 250 | 0 | Yes | 1 | 1 | 1 | 0
42 | [12 empty] | 250 | 0 | Yes | 1 | 1 | 1 | 0
43 | [12 empty] | 250 | 0 | Yes | 1 | 1 | 1 | 0
44 | [12 empty] | 250 | 0 | Yes | 1 | 1 | 1 | 0
45 | [12 empty] | 250 | 0 | Yes | 1 | 1 | 1 | 0
46 | [12 empty] | 250 | 0 | Yes | 1 | 1 | 1 | 0
47 | [12 empty] | 250 | 0 | Yes | 1 | 1 | 1 | 0
48 | [12 empty] | 250 | 0 | Yes | 1 | 1 | 1 | 0
49 | [12 empty] | 250 | 0 | Yes | 1 | 1 | 1 | 0
50 | [12 empty] | 250 | 0 | Yes | 1 | 1 | 1 | 0
Note on N9: Duplicate spaces are okay but they MUST have the same Total Existing Wattage of the Space.
Note on O9: If No is listed below the space (or total for the duplicate spaces) is over the allowed % of connected lighting load altered.
Compliance Main Page
Top of Page
9.1.2 Alterations Requirements

## Exterior Alterations
|  | Quick Links | ASHRAE/IES 90.1-2010 Lighting Compliance Documentation (v3.1)
Exterior Lighting Alterations (9.1.2 Alteration Exception)
| 90.1-2010 |  |  | 10%
Compliant
| In the yellow cells below select from Drop Down one of the spaces created in Step 2 on the Room Schedule page. (Duplicate spaces MUST have the same Total Existing Wattage and Total Square Footage.) |  | Total Existing Wattage of the Space | Max 9.1.2 exception wattage | Total square footage of the Space | Existing W/sf | Number of luminaires altered | Existing Luminaire Wattage (each) | Existing altered Wattage | Duplicate Space | Complies with 9.1.2 Exception?
0
1 | [12 empty] | 250 | 0 | Yes | 1 | 1 | 1 | 0
2 | [12 empty] | 250 | 0 | Yes | 1 | 1 | 1 | 0
3 | [12 empty] | 250 | 0 | Yes | 1 | 1 | 1 | 0
4 | [12 empty] | 250 | 0 | Yes | 1 | 1 | 1 | 0
5 | [12 empty] | 250 | 0 | Yes | 1 | 1 | 1 | 0
6 | [12 empty] | 250 | 0 | Yes | 1 | 1 | 1 | 0
7 | [12 empty] | 250 | 0 | Yes | 1 | 1 | 1 | 0
8 | [12 empty] | 250 | 0 | Yes | 1 | 1 | 1 | 0
9 | [12 empty] | 250 | 0 | Yes | 1 | 1 | 1 | 0
10 | [12 empty] | 250 | 0 | Yes | 1 | 1 | 1 | 0
11 | [12 empty] | 250 | 0 | Yes | 1 | 1 | 1 | 0
12 | [12 empty] | 250 | 0 | Yes | 1 | 1 | 1 | 0
13 | [12 empty] | 250 | 0 | Yes | 1 | 1 | 1 | 0
14 | [12 empty] | 250 | 0 | Yes | 1 | 1 | 1 | 0
15 | [12 empty] | 250 | 0 | Yes | 1 | 1 | 1 | 0
16 | [12 empty] | 250 | 0 | Yes | 1 | 1 | 1 | 0
17 | [12 empty] | 250 | 0 | Yes | 1 | 1 | 1 | 0
18 | [12 empty] | 250 | 0 | Yes | 1 | 1 | 1 | 0
19 | [12 empty] | 250 | 0 | Yes | 1 | 1 | 1 | 0
20 | [12 empty] | 250 | 0 | Yes | 1 | 1 | 1 | 0
21 | [12 empty] | 250 | 0 | Yes | 1 | 1 | 1 | 0
22 | [12 empty] | 250 | 0 | Yes | 1 | 1 | 1 | 0
23 | [12 empty] | 250 | 0 | Yes | 1 | 1 | 1 | 0
24 | [12 empty] | 250 | 0 | Yes | 1 | 1 | 1 | 0
25 | [12 empty] | 250 | 0 | Yes | 1 | 1 | 1 | 0
26 | [12 empty] | 250 | 0 | Yes | 1 | 1 | 1 | 0
27 | [12 empty] | 250 | 0 | Yes | 1 | 1 | 1 | 0
28 | [12 empty] | 250 | 0 | Yes | 1 | 1 | 1 | 0
29 | [12 empty] | 250 | 0 | Yes | 1 | 1 | 1 | 0
30 | [12 empty] | 250 | 0 | Yes | 1 | 1 | 1 | 0
31 | [12 empty] | 250 | 0 | Yes | 1 | 1 | 1 | 0
32 | [12 empty] | 250 | 0 | Yes | 1 | 1 | 1 | 0
33 | [12 empty] | 250 | 0 | Yes | 1 | 1 | 1 | 0
34 | [12 empty] | 250 | 0 | Yes | 1 | 1 | 1 | 0
35 | [12 empty] | 250 | 0 | Yes | 1 | 1 | 1 | 0
36 | [12 empty] | 250 | 0 | Yes | 1 | 1 | 1 | 0
37 | [12 empty] | 250 | 0 | Yes | 1 | 1 | 1 | 0
38 | [12 empty] | 250 | 0 | Yes | 1 | 1 | 1 | 0
39 | [12 empty] | 250 | 0 | Yes | 1 | 1 | 1 | 0
40 | [12 empty] | 250 | 0 | Yes | 1 | 1 | 1 | 0
41 | [12 empty] | 250 | 0 | Yes | 1 | 1 | 1 | 0
42 | [12 empty] | 250 | 0 | Yes | 1 | 1 | 1 | 0
43 | [12 empty] | 250 | 0 | Yes | 1 | 1 | 1 | 0
44 | [12 empty] | 250 | 0 | Yes | 1 | 1 | 1 | 0
45 | [12 empty] | 250 | 0 | Yes | 1 | 1 | 1 | 0
46 | [12 empty] | 250 | 0 | Yes | 1 | 1 | 1 | 0
47 | [12 empty] | 250 | 0 | Yes | 1 | 1 | 1 | 0
48 | [12 empty] | 250 | 0 | Yes | 1 | 1 | 1 | 0
49 | [12 empty] | 250 | 0 | Yes | 1 | 1 | 1 | 0
50 | [12 empty] | 250 | 0 | Yes | 1 | 1 | 1 | 0
Note on N9: Duplicate spaces are okay but they MUST have the same Total Existing Wattage of the Space and Total Square Footage.
Note on O9: If No is listed below the space (or total for the duplicate spaces) is over the allowed % of connected lighting load altered.
Compliance Main Page
Top of Page
9.1.2 Alterations Requirements

## 9.1.1
9.1.1 - Scope
9.1.1 Scope. This section shall apply to the following: a. interior spaces of buildings b. exterior building features, including facades, illuminated roofs, architectural features, entrances, exits, loading docks, and illuminated canopies c. exterior building grounds lighting provided through the building’s electrical service Exceptions: a. emergency lighting that is automatically off during normal building operation b. lighting within dwelling units c. lighting that is specifically designated as required by a health or life safety statute, ordinance, or regulation d. decorative gas lighting systems
Return to Top of Compliance Worksheet

## 9.1.2
9.1.2 - Lighting Alterations
9.1.2 Lighting Alterations. The alteration of lighting systems in any building space or exterior area shall comply with the lighting power density (LPD) requirements of Section 9 applicable to that space or area and the automatic shutoff requirements of 9.4.1.1. Such alterations shall include all luminaires that are added, replaced or removed. This requirement shall also be met for alterations that involve only the replacement of lamps plus ballasts. Alterations do not include routine maintenance or repair situations. Exception: Alterations that involve less than 10% of the connected lighting load in a space or area need not comply with these requirements provided that such alterations do not increase the installed LPD.
Return to Top of Compliance Worksheet
Return to Interior Alterations
Return to Exterior Alterations

## 9.1.3
9.1.3 - Installed Lighting Power
9.1.3 Installed Lighting Power. The luminaire wattage for all interior and exterior applications shall include all power used by the luminaires, including lamps, ballasts, transformers, and control devices except as specifically exempted in Section 9.1.1, 9.2.2.3, or 9.4.5. Exception: If two or more independently operating lighting systems in a space are capable of being controlled to prevent simultaneous user operation, the installed interior lighting power or the installed exterior lighting power shall be based solely on the lighting system with the highest wattage.
Return to Top of Compliance Worksheet

## 9.1.4
9.1.4 - Interior and Exterior Luminaire Wattage
9.1.4 Interior and Exterior Luminaire Wattage. Luminaire wattage, when used to calculate either installed interior lighting power or installed exterior lighting power, shall be determined in accordance with the following criteria: a. The wattage of line-voltage luminaires not containing permanently installed ballasts, transformers, or similar devices shall be the manufacturers’ labeled maximum wattage of the luminaire. b. The wattage of luminaires with permanently installed or remote ballasts, transformers, or similar devices shall be the operating input wattage of the maximum lamp/auxiliary combination based on values from the auxiliary manufacturers’ literature or recognized testing laboratories or shall be the maximum labeled wattage of the luminaire. Exception: Lighting power calculations for ballasts with adjustable ballast factors shall be based on the ballast factor that will be used in the space provided that the ballast factor is not user changeable. c. For line-voltage lighting track and plug-in busway, designed to allow the addition and/or relocation of luminaires without altering the wiring of the system, the wattage shall be: 1. the specified wattage of the luminaires included in the system with a minimum of 30 W/lin ft or 2. the wattage limit of the system’s circuit breaker or 3. the wattage limit of other permanent current-limiting device(s) on the system. d. The wattage of low-voltage lighting track, cable conductor, rail conductor, and other flexible lighting systems that allow the addition and/or relocation of luminaires without altering the wiring of the system shall be the specified wattage of the transformer supplying the system. e. The wattage of all other miscellaneous lighting equipment shall be the specified wattage of the lighting equipment.
Return to Top of Compliance Worksheet

## 9.2
9.2 - Compliance Paths
9.2 Compliance Path(s) 9.2.1 Lighting systems and equipment shall comply with Section 9.1, General; Section 9.4, Mandatory Provisions; and the prescriptive requirements of either: a. Section 9.5, Building Area Method; or b. Section 9.6, Space-by-Space Method. 9.2.2 Prescriptive Requirements 9.2.2.1 The Building Area Method for determining the interior lighting power allowance, described in Section 9.5, is a simplified approach for demonstrating compliance. 9.2.2.2 The Space-by-Space Method, described in Section 9.6, is an alternative approach that allows greater flexibility. 9.2.2.3 Interior Lighting Power. The interior lighting power allowance for a building or a separately metered or permitted portion of a building shall be determined by either the Building Area Method described in Section 9.5 or the Spaceby-Space Method described in Section 9.6. Trade-offs of interior lighting power allowance among portions of the building for which a different method of calculation has been used are not permitted. The installed interior lighting power identified in accordance with Section 9.1.3 shall not exceed the interior lighting power allowance developed in accordance with Section 9.5 or 9.6. Exceptions: The following lighting equipment and applications shall not be considered when determining the interior lighting power allowance developed in accordance with Section 9.5 or 9.6, nor shall the wattage for such lighting be included in the installed interior lighting power identified in accordance with Section 9.1.3. However, any such lighting shall not be exempt unless it is an addition to general lighting and is controlled by an independent control device. a. Display or accent lighting that is an essential element for the function performed in galleries, museums, and monuments. b. Lighting that is integral to equipment or instrumentation and is installed by its manufacturer. c. Lighting specifically designed for use only during medical or dental procedures and lighting integral to medical equipment. d. Lighting integral to both open and glass-enclosed refrigerator and freezer cases. e. Lighting integral to food warming and food preparation equipment. f. Lighting for plant growth or maintenance. g. Lighting in spaces specifically designed for use by occupants with special lighting needs including visual impairment and other medical and age-related issues. h. Lighting in retail display windows, provided the display area is enclosed by ceiling-height partitions. i. Lighting in interior spaces that have been specifically designated as a registered interior historic landmark. j. Lighting that is an integral part of advertising or directional signage. k. Exit signs. l. Lighting that is for sale or lighting educational demonstration systems. m. Lighting for theatrical purposes, including performance, stage, and film and video production. n. Lighting for television broadcasting in sporting activity areas. o. Casino gaming areas. p. Furniture-mounted supplemental task lighting that is controlled by automatic shutoff and complies with Section 9.4.1.6(d). q. Mirror lighting in dressing rooms and accent lighting in religious pulpit and choir areas. r. Parking garage transition lighting: Lighting for covered vehicle entrances and exits from buildings and parking structures, that comply with section 9.4.1.3 a and c. Each transition zone shall not exceed a depth of 66 ft inside the structure and a width of 50 ft.
Return to Top of Compliance Worksheet

## 9.4.1.1 (10)
9.4.1.1 - Automatic Lighting Shutoff
9.4.1.1 Automatic Lighting Shutoff. Interior lighting in buildings shall be controlled with an automatic control device to shut off building lighting in all spaces. This automatic control device shall function on either: a. a scheduled basis using a time-of-day operated control device that turns lighting off at specific programmed times—an independent program schedule shall be provided for areas of no more than 25,000 sq.ft but not more than one floor—or b. an occupant sensor that shall turn lighting off within 30 minutes of an occupant leaving a space, or c. a signal from another control or alarm system that indicates the area is unoccupied. Exceptions: The following shall not require an automatic control device: a. Lighting required for 24-hour operation. b. Lighting in spaces where patient care is rendered. c. Lighting in spaces where an automatic shutoff would endanger the safety or security of the room or building occupant(s). NOTE: Any automatic control device required in sections 9.4.1.1, 9.4.1.2, and 9.4.1.4 shall either be manual on or shall be controlled to automatically turn the lighting on to not more than 50% power, except in the following spaces where full automatic-on is allowed; a. public corridors and stairwells, b. restrooms, c. primary building entrance areas and lobbies, and d. areas where manual-on operation would endanger the safety or security of the room or building occupant(s).
Return to Top of Compliance Worksheet
Return to
Building Area
9.4.1.1
Return to
Space-by-Space 9.4.1.1

## 9.4.1.2
9.4.1.2 - Space Control
9.4.1.2 Space Control. Each space enclosed by ceiling height partitions shall have at least one control device to independently control the general lighting within the space. Each manual device shall be readily accessible and located so the occupants can see the controlled lighting. All controlled lighting shall meet the following requirements:
(a) The controlled lighting shall have at least one control step between 30% and 70% (inclusive) of full lighting power in addition to all off.
Exceptions to 9.4.1.2(a):
1. Lights in corridors, electrical/mechanical rooms, public lobbies, restrooms, stairways, and storage rooms
2. Spaces with only one luminaire with rated input power less than 100 W.
3. Spaces types with lighting power allowance of less than 0.6 W/sq.ft (see Table 9.6.1).
(b) An occupant sensor or a timer switch shall be installed that automatically turns lighting off within 30 minutes of all occupants leaving a space in:
1. classrooms and lecture halls,
2. conference, meeting, and training rooms,
3. employee lunch and break rooms,
4. storage and supply rooms between 50 sq.ft and 1000 sq.ft,
5. rooms used for document copying and printing,
6. office spaces up to 250 sq.ft,
7. restrooms, and
8. dressing, locker, and fitting rooms.
Exceptions to 9.4.1.2(b):
1. Spaces with multi-scene control systems,
2. shop and laboratory classrooms,
3. spaces where an automatic shutoff would endanger the safety or security of the room or building occupant(s),
4. lighting required for 24-hour operation.
(c) For spaces not included in 9.4.1.2b, each control device shall be activated either manually by an occupant or automatically by sensing an occupant. Each control device shall control a maximum of 2500 sq.ft area for a space 10,000 sq.ft or less and a maximum of 10,000 sq.ft area for a space greater than 10,000 sq.ft. The occupant shall be able to override any time-of-day scheduled shutoff control for no more than two hours.
Exception to 9.4.1.2c: Remote location shall be permitted for reasons of safety or security when the remote control
device has an indicator pilot light as part of or next to the control device and the light is clearly labeled to identify
the controlled lighting.
NOTE: Any automatic control device required in sections 9.4.1.1, 9.4.1.2, and 9.4.1.4 shall either be manual on or shall be controlled to automatically turn the lighting on to not more than 50% power, except in the following spaces where full automatic-on is allowed:
a. public corridors and stairwells,
b. restrooms,
c. primary building entrance areas and lobbies, and
d. areas where manual-on operation would endanger the safety or security of the room or building occupant(s).
Return to Top of Compliance Worksheet
Return to
Space-by-Space 9.4.1.2(a)
Return to
Building Area 9.4.1.2(a)
Return to
Space-by-Space 9.4.1.2(b)
Return to
Building Area 9.4.1.2(b)
Return to
Space-by-Space 9.4.1.2(c)
Return to
Building Area 9.4.1.2(c)

## 9.4.1.3
9.4.1.3 - Parking Garage Lighting Control
9.4.1.3 Parking Garage Lighting Control. Lighting for parking garages shall comply with the following requirements: a. Comply with Section 9.4.1.1. b. Lighting shall be controlled by one or more devices that automatically reduce lighting power of each luminaire by a minimum of 30% when there is no activity detected within a lighting zone for no more than 30 minutes. Lighting zones for this requirement shall be no larger than 3,600 sq.ft, c. Daylight transition zone lighting, as described in Section 9.2.2.3 exception r, shall be separately controlled by a device that automatically turns lighting on during daylight hours and off at sunset. d. For luminaires within 20 ft of any perimeter wall structure that has a net opening to wall ratio of at least 40% and no exterior obstructions within 20 ft, the power shall be automatically reduced in response to daylight. Exceptions: a. Daylight transitions zones and ramps without parking are exempt from sections b and d above. b. Applications using HID of 150 watts or less or Induction lamps are exempt from section b above.
Return to Top of Compliance Worksheet
Return to
Space-by-Space 9.4.1.3
Return to
Building Area Method 9.4.1.3

## 9.4.1.2-OLD (hidden)
| 9.4.1.2 Space Control | Return
Space Control. Each space enclosed by ceiling height partitions shall have at least one control device to independently control the general lighting within the space. Each manual device shall be readily accessible and located so the occupants can see the controlled lighting.
a. A control device shall be installed that automatically turns lighting off within 30 minutes of all occupants leaving a space, except spaces with multi-scene control, in
1. classrooms (not including shop classrooms, laboratory classrooms, and preschool through 12th grade classrooms),
2. conference/meeting rooms, and
3. employee lunch and break rooms.
b. These spaces are not required to be connected to other automatic lighting shutoff controls.
c. For all other spaces, each control device shall be activated either manually by an occupant or automatically by sensing an occupant. Each control device shall control a maximum of 2500 ft2 area for a space 10,000 ft2 or less and a maximum of 10,000 ft2 area for a space greater than 10,000 ft2 and be capable of overriding any time-of-day scheduled shutoff control for no more than four hours.
Exception: Remote location shall be permitted for reasons of safety or security when the remote control device has an indicator pilot light as part of or next to the control device and the light is clearly labeled to identify the controlled lighting.

## Project Worksheet (hidden)
Project Name:
Code Compliance Calculations for Lighting Based On:
Fixture Type | Lighting Description

## Luminaire_Schedule (hidden)
Project Name:
Code Compliance Calculations for Lighting Based On:
Fixture Type | Luminaire Description | Source(s) |  | Ballast(s) or Transformer(s) | Fixture Quantity |  | Fixture Input Watts Per Unit | Total Watts | Notes
[5 empty] | Count | Units | # Watts
L1 | Recessed 6" CFL downlight | 32W CFL |  | Lutron Hi-Lume 1% Dimming | 35 | EA | 36 | 1260
L2 | Surface mounted LED cove light | WW LED |  | Integral driver | 240 | LF | 5 | 1200
Note on A4: Acuity Brands Lighting: This column must be kept in alphabetical order.
Note on I5: Acuity Brands Lighting: EA = Each LF = Linear Feet

## 9.4.1.4
9.4.1.4 - Automatic Daylighting Controls for Primary Sidelighted Areas
9.4.1.4 Automatic Daylighting Controls for Primary Sidelighted Areas. When the combined primary sidelighted area in an enclosed space equals or exceeds 250 sq.ft, the lamps for general lighting in the primary sidelighted area shall be separately controlled by at least one multilevel photocontrol (including continuous dimming devices) having the following characteristics: a. the light sensor for the photocontrol shall be remote from where calibration adjustments are made; b. the calibration adjustments shall be readily accessible; and c. the multilevel photocontrol shall reduce electric lighting in response to available daylight with at least one control step that is between 50% and 70% of design lighting power and another control step that is no greater than 35% (including off) of design power. Exceptions: a. Primary sidelighted areas where the top of the existing adjacent structures are twice as high above the windows as their distance away from the windows b. Primary sidelighted areas where the sidelighting effective aperture is less than 0.1 (10%) c. retail spaces NOTE: Any automatic control device required in sections 9.4.1.1, 9.4.1.2, and 9.4.1.4 shall either be manual on or shall be controlled to automatically turn the lighting on to not more than 50% power, except in the following spaces where full automatic-on is allowed; a. public corridors and stairwells, b. restrooms, c. primary building entrance areas and lobbies, and d. areas where manual-on operation would endanger the safety or security of the room or building occupant(s).
Return to Top of Compliance Worksheet
Return to
Space-by-Space 9.4.1.4
Return to
Building Area
9.4.1.4

## 9.4.1.5
9.4.1.5 - Automatic Daylighting Controls for Toplighting
9.4.1.5 Automatic Daylighting Controls for Toplighting. When the total daylight area under skylights plus the total daylight area under rooftop monitors in an enclosed space exceeds 900 sq.ft, the lamps for general lighting in the daylight area shall be separately controlled by at least one multilevel photocontrol (including continuous dimming devices) having the following characteristics: a. the light sensor for the photocontrol shall be remote from where calibration adjustments are made, b. the calibration adjustments shall be readily accessible, and c. the multilevel photocontrol shall reduce electric lighting in response to available daylight with at least one control step that is between 50% and 70% of design lighting power and another control step that is no greater than 35% of design power. Exceptions: a. Daylighted areas under skylights where it is documented that existing adjacent structures or natural objects block direct beam sunlight for more than 1500 daytime hours per year between 8 a.m. and 4 p.m. b. Daylighted areas where the skylight effective aperture (EA) is less than 0.006 (0.6%). c. Buildings in climate zone 8 with daylight areas totaling less than 1,500 ft2 in an enclosed space.
Return to Top of Compliance Worksheet
Return to
Space-by-Space 9.4.1.5
Return to
Building Area
9.4.1.5

## 9.4.1.6
9.4.1.6 - Additional Control
9.4.1.6 Additional Control. Additional controls shall meet the following requirements: a. Display/Accent Lighting—display or accent lighting shall have a separate control device. b. Case Lighting—lighting in cases used for display purposes shall have a separate control device. c. Guest Room Lighting—Guestrooms in hotels, motels, boarding houses or similar buildings shall have one or more control device(s) at the entry door that collectively control all permanently installed luminaires and switched receptacles, except those in the bathroom(s). Suites shall have control(s) meeting these requirements at the entry to each room or at the primary entry to the suite. Bathrooms shall have a control device installed to automatically turn off the bathroom lighting, except for night lighting not exceeding 5 watts, within 60 minutes of the occupant leaving the space. d. Task Lighting—supplemental task lighting, including permanently installed undershelf or undercabinet lighting, shall have a control device integral to the luminaires or be controlled by a wall-mounted control device provided the control device is readily accessible and located so that the occupant can see the controlled lighting. e. Nonvisual Lighting—lighting for nonvisual applications, such as plant growth and food warming, shall have a separate control device. f. Demonstration Lighting—lighting equipment that is for sale or for demonstrations in lighting education shall have a separate control device. g. Stairwell Lighting—Lighting in stairwells shall have one or more control devices to automatically reduce lighting power in any one controlled zone by at least 50% within 30 minutes of all occupants leaving that controlled zone.
Return to Top of Compliance Worksheet
Return to
Space-by-Space 9.4.1.6
Return to
Building Area
9.4.1.6

## 9.4.1.7
9.4.1.7 - Exterior Lighting Control
9.4.1.7 Exterior Lighting Control. Lighting for exterior applications not exempted in section 9.1 shall meet the following requirements: a. Lighting shall be controlled by a device that automatically turns off the lighting when sufficient daylight is available. b. All building façade and landscape lighting shall be automatically shut off between midnight or business closing, whichever is later, and 6am or business opening, whichever comes first, or between times established by the authority having jurisdiction. c. Lighting not specified in section b above, including advertising signage, shall be controlled by a device that automatically reduces the connected lighting power by at least 30% for at least one of the following conditions: 1. from 12 midnight or within one (1) hour of the end of business operations, whichever is later, until 6am or business opening, whichever is earlier; or 2. during any period when no activity has been detected for a time of no longer than 15 minutes. All time switches shall be capable of retaining programming and the time setting during loss of power for a period of at least ten hours. Exception: Lighting for covered vehicle entrances or exits from buildings or parking structures where required for safety, security, or eye adaptation.
Return to Top of Compliance Worksheet
Return to Exterior Lighting Worksheet

## 9.4.2
9.4.2 - Exit Signs
9.4.2 Exit Signs. Internally illuminated exit signs shall not exceed 5 W per face.
Return to Luminaire Schedule
Return to Top of Compliance Worksheet

## 9.4.3
9.4.3 - Exterior Building Lighting Power
9.4.3 Exterior Building Lighting Power. The total exterior lighting power allowance for all exterior building applications is the sum of the base site allowance plus the individual allowances for areas that are designed to be illuminated and are permitted in Table 9.4.3B for the applicable lighting zone. The installed exterior lighting power identified in accordance with Section 9.1.3 shall not exceed the exterior lighting power allowance developed in accordance with this section. Trade-offs are allowed only among exterior lighting applications listed in the Table 9.4.3B “Tradable Surfaces” section. The lighting zone for the building exterior is determined from Table 9.4.3A unless otherwise specified by the local jurisdiction. Exceptions: Lighting used for the following exterior applications is exempt when equipped with a control device that complies with the requirements of Section 9.4.1.7 and is independent of the control of the nonexempt lighting: a. Specialized signal, directional, and marker lighting associated with transportation. b. Advertising signage or directional signage. c. Lighting integral to equipment or instrumentation and installed by its manufacturer. d. Lighting for theatrical purposes, including performance, stage, film production, and video production. e. Lighting for athletic playing areas. f. Temporary lighting. g. Lighting for industrial production, material handling, transportation sites, and associated storage areas. h. Theme elements in theme/amusement parks. i. Lighting used to highlight features of public monuments and registered historic landmark structures or buildings. j. Lighting for hazardous locations. k. Lighting for swimming pools and water features. l. Searchlights.
Return to Top of Compliance Worksheet
Link to Exterior Lighting Worksheet

## 9.4.4
9.4.4 - Functional Testing
9.4.4 Functional Testing. Lighting control devices and control systems shall be tested to ensure that control hardware and software are calibrated, adjusted, programmed, and in proper working condition in accordance with the construction documents and manufacturer’s installation instructions. When occupant sensors, time switches, programmable schedule controls, or photosensors are installed, at a minimum, the following procedures shall be performed: a. Confirm that the placement, sensitivity and time-out adjustments for occupant sensors yield acceptable performance, lights turn off only after space is vacated and do not turn on unless space is occupied. b. Confirm that the time switches and programmable schedule controls are programmed to turn the lights off. c. Confirm that photosensor controls reduce electric light levels based on the amount of usable daylight in the space as specified. The construction documents shall state the party who will conduct and certify the functional testing. The party responsible for the functional testing shall not be directly involved in either the design or construction of the project and shall provide documentation certifying that the installed lighting controls meet or exceed all documented performance criteria. Certification shall be specific enough to verify conformance.
Return to Top of Compliance Worksheet

## 9.5
9.5 - Building Area Method Compliance Path
9.5 Building Area Method Compliance Path 9.5.1 Building Area Method of Calculating Interior Lighting Power Allowance. Use the following steps to determine the interior lighting power allowance by the Building Area Method: a. Determine the appropriate building area type from Table 9.5.1 and the allowed LPD (watts per unit area) from the “Building Area Method” column. For building area types not listed, selection of a reasonably equivalent type shall be permitted. b. Determine the gross lighted floor area (square feet) of the building area type. c. Multiply the gross lighted floor areas of the building area type(s) times the LPD. d. The interior lighting power allowance for the building is the sum of the lighting power allowances of all building area types. Trade-offs among building area types are permitted provided that the total installed interior lighting power does not exceed the interior lighting power allowance.
Return to Top of Compliance Worksheet
Return to Building Area Method Worksheet

## 9.6
9.6 - Alternative Compliance Path: Space-by-Space Method
9.6 Alternative Compliance Path: Space-by-Space Method 9.6.1 Space-by-Space Method of Calculating Interior Lighting Power Allowance. Use the following steps to determine the interior lighting power allowance by the Space-by-Space Method: a. For each space enclosed by partitions that are 80% of the ceiling height or taller, determine the appropriate space type from Table 9.6.1. If a space has multiple functions, where more than one space type is applicable, that space shall be broken up into smaller subspaces, each using their own space type from Table 9.6.1. Any of these subspaces that are smaller in floor area than 20% of the original space and less than 1000 sq.ft need not be broken out separately. Include the floor area of balconies and other projections in this calculation. b. In calculating the area of each space and subspace, the limits of the area are defined by the centerline of interior walls, the dividing line between subspaces, and the outside surface of exterior walls. c. Based on the space type selected for each space or subspace, determine the lighting power allowance of each space or subspace by multiplying the calculated area of the space or subspace by the appropriate LPD determined in 9.6.1(a). For space types not listed, selection of a reasonable equivalent category shall be permitted. d. The interior lighting power allowance is the sum of lighting power allowances of all spaces and subspaces. Tradeoffs among spaces and subspaces are permitted provided that the total installed interior lighting power does not exceed the interior lighting power allowance.
9.6.2 Additional Interior Lighting Power. When using the Space-by-Space Method, an increase in the interior lighting power allowance is allowed for specific lighting functions. Additional power shall be allowed only if the specified lighting is installed and automatically controlled, separately from the general lighting, to be turned off during nonbusiness hours. This additional power shall be used only for the specified luminaires and shall not be used for any other purpose, unless otherwise indicated. An increase in the interior lighting power allowance is permitted in the following cases:
a. For spaces in which lighting is specified to be installed in addition to the general lighting for the purpose of decorative appearance or for highlighting art or exhibits, provided that the additional lighting power shall not exceed 1.0 W/sqft of such spaces.
b. For lighting equipment installed in sales areas and specifically designed and directed to highlight merchandise, calculate the additional lighting power as follows: Additional Interior Lighting Power Allowance = 1000 watts + (Retail Area 1 × 0.6 W/sq.ft) + (Retail Area 2 × 0.6 W/sq.ft) + (Retail Area 3 × 1.4 W/sq.ft) + (Retail Area 4 × 2.5 W/sq.ft), where Retail Area 1 = the floor area for all products not listed in Retail Areas 2, 3, or 4; Retail Area 2 = the floor area used for the sale of vehicles, sporting goods, and small electronics; Retail Area 3 = the floor area used for the sale of furniture, clothing, cosmetics, and artwork; and Retail Area 4 = the floor area used for the sale of jewelry, crystal, and china. Exception: Other merchandise categories may be included in Retail Areas 2 through 4 above, provided that justification documenting the need for additional lighting power based on visual inspection, contrast, or other critical display is approved by the authority having jurisdiction. c. For space types identified in Table 9.6.2, when additional controls are used as indicated, provided that all mandatory controls are used according to Section 9.4, the additional lighting power, to be used anywhere in the building, is calculated as follows: Additional Interior Lighting Power Allowance = Lighting Power Under Control × Control Factor; where: Lighting Power Under Control = the total wattage of all lighting fixtures that are controlled in the given space using the control method indicated Control Factor = the value given in Table 9.6.2 for the corresponding space type and control method.
c. For space types identified in Table 9.6.2, when additional controls are used as indicated, provided that all mandatory controls are used according to Section 9.4, the additional lighting power, to be used anywhere in the building, is calculated as follows: Additional Interior Lighting Power Allowance = Lighting Power Under Control × Control Factor; where: Lighting Power Under Control = the total wattage of all lighting fixtures that are controlled in the given space using the control method indicated Control Factor = the value given in Table 9.6.2 for the corresponding space type and control method.
Return to Top of Compliance Worksheet
Return to Space by Space Step a
Return to Space by Space Decorative
Return to Space by Space Retail

## 9.6.2c
Table 9.6.2 Control Factors in Calculating Additional Lighting Power Allowance
Method # | Description | Open Office | Private Office | Conference Room, Meeting Room, Classroom (Lecture/Training) | Retail Sales Area | Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage | NA
01 | Manual, continuous dimming control or Programmable multi-level dimming control | 0.05 | 0.05 | 0.1 | 0.1 | 0 | 0
02 | Programmable multi-level dimming control using programmable time scheduling | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0
03 | Multi-level occupancy sensors | 0.05 | 0.05 | 0.05 | 0 | 0 | 0
04 | Occupancy sensors controlling the downlight component of workstation specific luminaires with continuous dimming to off capabilities. | 0.25 | 0 | 0 | 0 | 0 | 0
05 | Occupancy sensors controlling the downlight component of workstation specific luminaires with continuous dimming to off operation, in combination with personal continuous dimming control of downlight illumination by workstation occupant. | 0.3 | 0 | 0 | 0 | 0 | 0
06 | Automatic bi-level or multi-level switching in primary sidelighted areas when sidelighting effective aperture is greater than 0.15 | 0 | 0 | 0 | 0.1 | 0 | 0
07 | Automatic bi-level or multi-level switching in primary sidelighted areas when sidelighting effective aperture is greater than 0.15 and when primary sidelighted area is less than 250 sq.ft | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0
08 | Automatic continuous daylight dimming in primary sidelighted areas when sidelighting effective aperture is greater than 0.15 and when primary sidelighted area is less than 250 sq.ft | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0
09 | Automatic continuous daylight dimming in primary sidelighted areas when sidelighting effective aperture is greater than 0.15 and when primary sidelighted area is greater than 250 sq.ft | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0
10 | Automatic continuous daylight dimming in secondary sidelighted areas when sidelighting effective aperture is greater than 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0
11 | Automatic continuous daylight dimming in daylighted areas under skylights when the total of those areas is less than 900 sq.ft and when skylight effective aperture is greater than 0.01 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0
12 | Automatic continuous daylight dimming in daylighted areas under skylights when the total of those areas is greater than 900 sq.ft and when skylight effective aperture is greater than 0.01 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0
Footnotes
1 | These control factors may only be used if the requirements of section 9.4.1.2 are met using an occupancy sensor.
2 | Control factor is limited to the wattage of workstation-specific luminaires in partitioned single occupant workspaces contained within an open office environment (i.e. direct-indirect luminaires with separately controlled downlight and uplight components, with the downward component providing illumination to a single occupant in an open plan workstation). Within 30 minutes of the occupant leaving the space, the downward component shall continuously dim to off over a minimum of 2 minutes. Upon the occupant entering the space, the downward component shall turn on at the minimum level and continuously raise the illumination to a preset level over a minimum of 30 seconds. The uplight component of workstation specific luminaire shall comply with section 9.4.1.1 (automatic shutoff).
3 | In addition to the requirements described in footnote 2, the control shall allow the occupant to select their preferred light level via a personal computer, handheld device, or similarly accessible device located within the workstation.
4 | Control factors may not be used if controls are used to satisfy exceptions to Section 5.5.4.2.3
| Open Office | 1
| Private Office | 2
| Conference Room, Meeting Room, Classroom (Lecture/Training) | 3
| Retail Sales Area | 4
| Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage | 5
| NA | 6
[8 empty] | Method # | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
[8 empty] | Description | Manual, continuous dimming control or Programmable multi-level dimming control | Programmable multi-level dimming control using programmable time scheduling | Multi-level occupancy sensors | Occupancy sensors controlling the downlight component of workstation specific luminaires with continuous dimming to off capabilities. | Occupancy sensors controlling the downlight component of workstation specific luminaires with continuous dimming to off operation, in combination with personal continuous dimming control of downlight illumination by workstation occupant. | Automatic bi-level or multi-level switching in primary sidelighted areas when sidelighting effective aperture is greater than 0.15 | Automatic bi-level or multi-level switching in primary sidelighted areas when sidelighting effective aperture is greater than 0.15 and when primary sidelighted area is less than 250 sq.ft | Automatic continuous daylight dimming in primary sidelighted areas when sidelighting effective aperture is greater than 0.15 and when primary sidelighted area is less than 250 sq.ft | Automatic continuous daylight dimming in primary sidelighted areas when sidelighting effective aperture is greater than 0.15 and when primary sidelighted area is greater than 250 sq.ft | Automatic continuous daylight dimming in secondary sidelighted areas when sidelighting effective aperture is greater than 0.3 | Automatic continuous daylight dimming in daylighted areas under skylights when the total of those areas is less than 900 sq.ft and when skylight effective aperture is greater than 0.01 | Automatic continuous daylight dimming in daylighted areas under skylights when the total of those areas is greater than 900 sq.ft and when skylight effective aperture is greater than 0.01
[8 empty] | Open Office | 0.05 | 0.05 | 0.05 | 0.25 | 0.3 | 0 | 0.1 | 0.2 | 0.1 | 0.1 | 0.2 | 0.1
[8 empty] | Private Office | 0.05 | 0.05 | 0.05 | 0 | 0 | 0 | 0.1 | 0.2 | 0.1 | 0.1 | 0.2 | 0.1
[8 empty] | Conference Room, Meeting Room, Classroom (Lecture/Training) | 0.1 | 0.1 | 0.05 | 0 | 0 | 0 | 0.1 | 0.2 | 0.1 | 0.1 | 0.2 | 0.1
[8 empty] | Retail Sales Area | 0.1 | 0.1 | 0 | 0 | 0 | 0.1 | 0.1 | 0.2 | 0.1 | 0.1 | 0.2 | 0.1
[8 empty] | Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage | 0 | 0.1 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.1 | 0.1 | 0.2 | 0.1
Note on C7: See footnote 2.
Note on C8: See footnote 3.
Note on C9: See footnote 4.
Note on F4: See footnote 1
Note on F5: These control factors may only be used if the requirements of section 9.4.1.2 are met using an occupancy sensor.
Note on T48: See footnote 1
Note on U48: These control factors may only be used if the requirements of section 9.4.1.2 are met using an occupancy sensor.
Note on W45: See footnote 2.
Note on X45: See footnote 3.
Note on Y45: See footnote 4.
Return to Top of Compliance Worksheet
Return to Control selection

## 9.7
9.7 - Submittals
9.7 Submittals 9.7.1 General. Where required by the authority having jurisdiction the submittal of compliance documentation and supplemental information shall be in accordance with section 4.2.2. 9.7.2 Completion requirements. The following requirements are mandatory provisions and are necessary for compliance with this standard. 9.7.2.1 Drawings. Construction documents shall require that within 90 days after the date of system acceptance, record drawings of the actual installation be provided to the building owner or the designated representative of the building owner. Record drawings shall include, as a minimum, the location, luminaire identifier, control, and circuiting for each piece of lighting equipment. 9.7.2.2 Manuals. Construction documents shall require for all lighting equipment and lighting controls, an operating and maintenance manual be provided to the building owner or the designated representative of the building owner within 90 days after the date of system acceptance. These manuals shall include, at a minimum, the following: a. Submittal data indicating all selected options for each piece of lighting equipment and lighting controls. b. Operation and maintenance manuals for each piece of lighting equipment and lighting controls with routine maintenance clearly identified including, as a minimum, a recommended relamping program and a schedule for inspecting and recalibrating all lighting controls. c. A complete narrative of how each lighting control system is intended to operate including recommended settings.
Return to Top of Compliance Worksheet

## LISTS (hidden)
Compliance Codes (ComCodes) |  |  | Building Types (BuildingType) | LPD |  | Space-by-Space Building Types (SBuildingType) | [14 empty] | Units | Current | LZ0 | LZ1 | LZ2 | LZ3 | LZ4 | Units | 1 | Control Types
90.1-2001 |  |  | Automotive Facility | 0.82 |  | 1-Common Space Types | [5 empty] | Manual, continuous dimming control or Programmable multi-level dimming control | [7 empty] | Base Allowance |  | #N/A | 0 | 500 | 600 | 750 | 1300 | watts | 2 | Building Automation
[8 empty] | Yes |  |  |  | Programmable multi-level dimming control using programmable time scheduling | [7 empty] | TRADABLE SURFACES | [8 empty] | 3 | Daylight Continuous Dimming
90.1-2004 |  |  | Convention Center | 1.08 |  | 2-Automotive |  | No |  |  |  | Multi-level occupancy sensors | [7 empty] | Uncovered parking areas and drives | sq.ft | #N/A | 0 | 0.04 | 0.06 | 0.1 | 0.13 | w/sq.ft | 4 | Daylight Step Dimming
90.1-2007 |  |  | Courthouse | 1.05 |  | 2-Bank/Office |  | Exempt |  |  |  | Occupancy sensors controlling the downlight component of workstation specific luminaires with continuous dimming to off capabilities. | [7 empty] | Walkways < 10' wide | lin.ft | #N/A | 0 | 0.7 | 0.7 | 0.8 | 1 | w/lin.ft | 5 | Occupancy Sensor
90.1-2010 |  |  | Dining: Bar Lounge/Leisure | 0.99 |  | 2-Convention Center |  | NA |  |  |  | Occupancy sensors controlling the downlight component of workstation specific luminaires with continuous dimming to off operation, in combination with personal continuous dimming control of downlight illumination by workstation occupant. | [7 empty] | Walkways ≥ 10' wide OR plazas | sq.ft | #N/A | 0 | 0.14 | 0.14 | 0.16 | 0.2 | w/sq.ft | 6 | Occupancy & Daylight sensors
|  |  | Dining: Cafeteria/Fast Food | 0.9 |  | 2-Courthouse/Police Station/Penitentiary | [5 empty] | Automatic bi-level or multi-level switching in primary sidelighted areas when sidelighting effective aperture is greater than 0.15 | [7 empty] | Stairways | sq.ft | #N/A | 0 | 0.75 | 1 | 1 | 1 | w/sq.ft | 7 | Timer Switch
Fixture Quantity Units (FQUnits) |  |  | Dining: Family | 0.89 |  | 2-Dormitory | [5 empty] | Automatic bi-level or multi-level switching in primary sidelighted areas when sidelighting effective aperture is greater than 0.15 and when primary sidelighted area is less than 250 sq.ft | [7 empty] | Pedestrian tunnels | sq.ft | #N/A | 0 | 0.15 | 0.15 | 0.2 | 0.3 | w/sq.ft | 8 | Vacancy Sensor
EA | count |  | Dormitory | 0.61 |  | 2-Fire Stations | [5 empty] | Automatic continuous daylight dimming in primary sidelighted areas when sidelighting effective aperture is greater than 0.15 and when primary sidelighted area is less than 250 sq.ft | [7 empty] | Landscaping | sq.ft | #N/A | 0 | 0.04 | 0.05 | 0.05 | 0.05 | w/sq.ft | 9 | Exterior Photocell
LF | linear feet |  | Exercise Center | 0.88 |  | 2-Gymnasium/Fitness Center | [5 empty] | Automatic continuous daylight dimming in primary sidelighted areas when sidelighting effective aperture is greater than 0.15 and when primary sidelighted area is greater than 250 sq.ft | [7 empty] | Main entries | lin.ft | #N/A | 0 | 20 | 20 | 30 | 30 | w/lin.ft | 10 | Astronomical Time Switch
|  |  | Fire Station | 0.71 |  | 2-Hospital | [5 empty] | Automatic continuous daylight dimming in secondary sidelighted areas when sidelighting effective aperture is greater than 0.3 | [7 empty] | Other doors | lin.ft | #N/A | 0 | 20 | 20 | 20 | 20 | w/lin.ft | 11 | Dimmer
YES/NO (YesNo) |  |  | Gymnasium | 1 |  | 2-Hotel/Motel | [5 empty] | Automatic continuous daylight dimming in daylighted areas under skylights when the total of those areas is less than 900 sq.ft and when skylight effective aperture is greater than 0.01 | [7 empty] | Entry canopies | sq.ft | #N/A | 0 | 0.25 | 0.25 | 0.4 | 0.4 | w/sq.ft | 12 | Multi-Scene Control
YES |  |  | Health-care Clinic | 0.87 |  | 2-Library | [5 empty] | Automatic continuous daylight dimming in daylighted areas under skylights when the total of those areas is greater than 900 sq.ft and when skylight effective aperture is greater than 0.01 | [7 empty] | Sales canopies | sq.ft | #N/A | 0 | 0.6 | 0.6 | 0.8 | 1 | w/sq.ft | 13 | 9.6.2c - Method 01
NO |  |  | Hospital | 1.21 |  | 2-Manufacturing | [13 empty] | Open sales areas | sq.ft | #N/A | 0 | 0.25 | 0.25 | 0.5 | 0.7 | w/sq.ft | 14 | 9.6.2c - Method 02
|  |  | Hotel | 1 |  | 2-Museum | [13 empty] | Street frontage | lin.ft | #N/A | 0 | 0 | 10 | 10 | 30 | w/lin.ft | 15 | 9.6.2c - Method 03
YES/NO/NA (YesNoNA) |  |  | Library | 1.18 |  | 2-Parking Garage | [13 empty] | NONTRADABLE SURFACES | [8 empty] | 16 | 9.6.2c - Method 04
YES |  |  | Manufacturing Facility | 1.11 |  | 2-Post Office | [13 empty] | Building facades by area | sq.ft | #N/A | 0 | 0 | 0.1 | 0.15 | 0.2 | w/sq.ft | 17 | 9.6.2c - Method 05
NO |  |  | Motel | 0.88 |  | 2-Religious Buildings | [13 empty] | Building facades by length | lin.ft | #N/A | 0 | 0 | 2.5 | 3.75 | 5 | w/lin.ft | 18 | 9.6.2c - Method 06
NA |  |  | Motion Picture Theater | 0.83 |  | 2-Retail | [13 empty] | ATMs & night depository location | locations | #N/A | 0 | 270 | 270 | 270 | 270 | watts | 19 | 9.6.2c - Method 07
|  |  | Multifamily | 0.6 |  | 2-Sports Arena | [13 empty] | Additional ATMs | additional ATMs | #N/A | 0 | 90 | 90 | 90 | 90 | watts | 20 | 9.6.2c - Method 08
|  |  | Museum | 1.06 |  | 2-Transportation | [13 empty] | Uncovered entrances & gatehouse inspection facilities at guarded facilities | sq.ft | #N/A | 0 | 0.75 | 0.75 | 0.75 | 0.75 | w/sq.ft | 21 | 9.6.2c - Method 09
Source Type (SourceType) |  |  | Office | 0.9 |  | 2-Warehouse | [13 empty] | Uncovered loading areas for law enforcement, fire, ambulance, and other emergency service vehicles | sq.ft | #N/A | 0 | 0.5 | 0.5 | 0.5 | 0.5 | w/sq.ft | 22 | 9.6.2c - Method 10
|  |  | Parking Garage | 0.25 | [15 empty] | Drive-through windows/doors (per drive through) | drive-throughs | #N/A | 0 | 400 | 400 | 400 | 400 | watts | 23 | 9.6.2c - Method 11
|  |  | Penitentiary | 0.97 | [15 empty] | Parking near 24-hour retail entrances | entrances | #N/A | 0 | 800 | 800 | 800 | 800 | watts | 24 | 9.6.2c - Method 12
|  |  | Performing Arts Theater | 1.39 | [7 empty] | Space Types (SSpaceType3) | LPD | RCR | Bi-Level | Occ |  |  |  | Roadway/parking entry, trail head, and toilet facility, or other locations approved by the authority having jurisdiction. | locations | #N/A | 60 | 0 | 0 | 0 | 0 | watts | 25
|  |  | Police | 0.96 |  | Atrium (first 40' in height) | 0.03/foot in height
|  |  | Post Office | 0.87 |  | Atrium ( height above 40') | 0.02/foot in height |  | LED |  | Atrium | C-Atrium | .03/.02 | na | No | No | Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage
|  |  | Religious Building | 1.05 |  | Audience/Seating Area - Auditorium | 0.79 |  | Fluorescent |  | Audience/Seating Area - Auditorium | C-Audience/Seating Area - Auditorium | 0.79 | 6 | Yes | No | NA |  |  | TABLE 9.4.2-1 Exterior Lighting Zones
|  |  | Retail | 1.4 |  | Audience/Seating Area - Motion Picture Theater | 1.14 |  | High Pressure Sodium |  | Audience/Seating Area - Motion Picture Theater | C-Audience/Seating Area - Motion Picture Theater | 1.14 | 4 | Yes | No | NA |  |  | Lighting Zone | Description
|  |  | School/University | 0.99 |  | Audience/Seating Area - Performing Arts Theater | 2.43 |  | Metal Halide |  | Audience/Seating Area - Performing Arts Theater | C-Audience/Seating Area - Performing Arts Theater | 2.43 | 8 | Yes | No | NA |  |  | 0 | Undeveloped areas within national parks, state parks, forest land, rural areas, and other undeveloped areas as defined by the authority having jurisdiction
Retail Area Type (RetailType) |  |  | Sports Arena | 0.78 |  | Classroom/Lecture/Training | 1.24 |  | Mercury Vapor |  | Classroom/Lecture/Training | C-Classroom/Lecture/Training | 1.24 | 4 | Yes | Yes | Conference Room, Meeting Room, Classroom (Lecture/Training)
1 | 0.6 |  | Town Hall | 0.92 |  | Conference/Meeting/Multipurpose | 1.23 |  | Low Pressure Sodium |  | Conference/Meeting/Multipurpose | C-Conference/Meeting/Multipurpose | 1.23 | 6 | Yes | Yes | Conference Room, Meeting Room, Classroom (Lecture/Training) |  |  | 1 | Developed areas of national parks, state parks, forest land, and rural areas
2 | 0.6 |  | Transportation | 0.77 |  | Corridor/Transition | 0.66 |  | Incandescent |  | Corridor/Transition | C-Corridor/Transition | 0.66 | 8' wide | No | No | Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage |  |  | 2 | Areas predominantly consisting of residential zoning, neighborhood business districts, light industrial with limited nighttime use and residential mixed use areas
3 | 1.4 |  | Warehouse | 0.66 |  | Dining Area | 0.65 |  | Induction |  | Dining Area | C-Dining Area | 0.65 | 4 | Yes | No | Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage
4 | 2.5 |  | Workshop | 1.2 |  | Dining Area - Bar Lounge/Leisure Dining | 1.31 |  | Plasma |  | Dining Area - Bar Lounge/Leisure Dining | C-Dining Area - Bar Lounge/Leisure Dining | 1.31 | 4 | Yes | No | Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage |  |  | 3 | All other areas
[6 empty] | Dining Area - Family Dining | 0.89 |  | Other |  | Dining Area - Family Dining | C-Dining Area - Family Dining | 0.89 | 4 | Yes | No | Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage |  |  | 4 | High-activity commercial districts in major metropolitan areas as designated by the local jurisdiction
Control Methods | [5 empty] | Dressing/Fitting Room - Performing Arts Theater | 0.4 |  |  |  | Dressing/Fitting Room - Performing Arts Theater | C-Dressing/Fitting Room - Performing Arts Theater | 0.4 | 6 | Yes | Yes | NA
1 |  | Open office |  |  |  | Electrical/Mechanical Room | 0.95 |  |  |  | Electrical/Mechanical Room | C-Electrical/Mechanical Room | 0.95 | 6 | No | No | NA
2 |  | Private office |  |  |  | Food Preperation | 0.99 |  |  |  | Food Preperation | C-Food Preperation | 0.99 | 6 | Yes | No | NA
3 |  | Conference Room |  |  |  | Laboratory - Classroom | 1.28 |  |  |  | Laboratory - Classroom | C-Laboratory - Classroom | 1.28 | 6 | Yes | Yes | Conference Room, Meeting Room, Classroom (Lecture/Training)
4 |  | Meeting Room |  |  |  | Laboratory - Research | 1.81 |  |  |  | Laboratory - Research | C-Laboratory - Research | 1.81 | 6 | Yes | No | NA |  | LZ0 | LZ0 - Undeveloped areas within national parks, state parks, forest land, rural areas, and other undeveloped areas as defined by the authority having jurisdiction
5 |  | Classroom (Lecture/Training) |  |  |  | Lobby | 0.64 |  |  |  | Lobby | C-Lobby | 0.9 | 4 | No | No | Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage |  | LZ1 | LZ1 - Developed areas of national parks, state parks, forest land, and rural areas
6 |  | Retail Sales Area |  |  |  | Lobby - Motion Picture Theater | 0.52 |  |  |  | Lobby - Motion Picture Theater | C-Lobby - Elevator | 0.64 | 6 | No | No | Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage |  | LZ2 | LZ2 - Areas predominantly consisting of residential zoning, neighborhood business districts, light industrial with limited nighttime use and residential mixed use areas
7 |  | Lobby |  |  |  | Lobby - Performing Arts Theater | 2 |  |  |  | Lobby - Performing Arts Theater | C-Lobby - Motion Picture Theater | 0.52 | 4 | No | No | Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage |  | LZ3 | LZ3 - All other areas
8 |  | Atrium |  |  |  | Locker Room | 0.75 |  |  |  | Locker Room | C-Lobby - Performing Arts Theater | 2 | 6 | No | No | Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage |  | LZ4 | LZ4 - High activity commercial districts in major metropolitan areas as designated by the local jurisdiction
9 |  | Dining Area |  |  |  | Lounge/Recreation | 0.73 |  |  |  | Lounge/Recreation | C-Locker Room | 0.75 | 6 | Yes | Yes | NA
10 |  | Stairways |  |  |  | Office-Enclosed | 1.11 |  |  |  | Office-Enclosed | C-Lounge/Recreation | 0.73 | 4 | Yes | Yes | NA
11 |  | Gym |  |  |  | Office-Open | 0.98 |  |  |  | Office-Open | C-Office-Enclosed | 1.11 | 8 | Yes | Yes | Private Office
12 |  | Pool |  |  |  | Restrooms | 0.98 |  |  |  | Restrooms | C-Office-Open | 0.98 | 4 | Yes | No | Open Office
|  | Mall Concourse |  |  |  | Sales Area | 1.68 |  |  |  | Sales Area | C-Restrooms | 0.98 | 8 | No | Yes | NA
|  | Parking Garage |  |  |  | Stairway | 0.69 |  |  |  | Stairway | C-Sales Area | 1.68 | 6 | Yes | No | Retail Sales Area
[6 empty] | Storage | 0.63 |  |  |  | Storage | C-Stairway | 0.69 | 10 | No | No | Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage
[6 empty] | Workshop | 1.59 |  |  |  | Workshop | C-Storage | 0.63 | 6 | No | Yes | NA
[5 empty] | x | Laboratory - Classroom | 1.4 |  | Automotive | Service/Repair | Automotive - Service/Repair | C-Workshop | 1.59 | 6 | Yes | No | NA
[5 empty] | x | Laboratory - Research | 1.4 |  | Bank/Office | Banking Activity Area | Bank/Office - Banking Activity Area | S-Automotive - Service/Repair | 0.67 | 4 | Yes | No | NA
[5 empty] | x | Lobby | 1.3 |  | Convention Center | Audience Seating | Convention Center - Audience Seating | S-Bank/Office - Banking Activity Area | 1.38 | 6 | Yes | No | NA
[5 empty] | x | Lobby - Hotel | 1.1 |  | Convention Center | Exhibit Space | Convention Center - Exhibit Space | S-Convention Center - Audience Seating | 0.82 | 4 | Yes | No | NA
[5 empty] | x | Lobby - Motion Picture Theater | 1.1 |  | Courthouse/Police Station/Penitentiary | Confinement Cells | Courthouse/Police Station/Penitentiary - Confinement Cells | S-Convention Center - Exhibit Space | 1.45 | 4 | Yes | No | NA
[5 empty] | x | Lobby - Performing Arts Theater | 3.3 |  | Courthouse/Police Station/Penitentiary | Courtroom | Courthouse/Police Station/Penitentiary - Courtroom | S-Courthouse/Police Station/Penitentiary - Confinement Cells | 1.1 | 6 | Yes | No | NA
[5 empty] | x | Locker Room | 0.6 |  | Courthouse/Police Station/Penitentiary | Judges' Chambers | Courthouse/Police Station/Penitentiary - Judges' Chambers | S-Courthouse/Police Station/Penitentiary - Courtroom | 1.72 | 6 | Yes | No | NA
[5 empty] | x | Lounge/Recreation | 1.2 |  | Courthouse/Police Station/Penitentiary | Penitentiary Audience Seating | Courthouse/Police Station/Penitentiary - Penitentiary Audience Seating | S-Courthouse/Police Station/Penitentiary - Judges' Chambers | 1.17 | 8 | Yes | No | NA
[5 empty] | x | Lounge/Recreation - Hospital | 0.8 |  | Courthouse/Police Station/Penitentiary | Penitentiary Dining | Courthouse/Police Station/Penitentiary - Penitentiary Dining | S-Courthouse/Police Station/Penitentiary - Penitentiary Audience Seating | 0.43 | 4 | Yes | No | NA
[5 empty] | x | Office-Enclosed | 1.1 |  | Courthouse/Police Station/Penitentiary | Pentitentiary Classroom | Courthouse/Police Station/Penitentiary - Pentitentiary Classroom | S-Courthouse/Police Station/Penitentiary - Penitentiary Dining | 1.07 | 6 | Yes | No | NA
[5 empty] | x | Office-Open | 1.1 |  | Dormitory | Living Quarters | Dormitory - Living Quarters | S-Courthouse/Police Station/Penitentiary - Pentitentiary Classroom | 1.34 | 4 | Yes | No | NA
[5 empty] | x | Restrooms | 0.9 |  | Fire Stations | Engine Room | Fire Stations - Engine Room | S-Dormitory - Living Quarters | 0.38 | 8 | Yes | No | NA
[5 empty] | x | Sales Area | 1.7 |  | Fire Stations | Sleeping Quarters | Fire Stations - Sleeping Quarters | S-Fire Stations - Engine Room | 0.56 | 4 | Yes | No | NA
[5 empty] | x | Stairway | 0.6 |  | Gymnasium/Fitness Center | Fitness Area | Gymnasium/Fitness Center - Fitness Area | S-Fire Stations - Sleeping Quarters | 0.25 | 6 | Yes | No | NA
[5 empty] | x | Storage | 0.8 |  | Gymnasium/Fitness Center | Fitness Center - Audience Seating | Gymnasium/Fitness Center - Fitness Center - Audience Seating | S-Gymnasium/Fitness Center - Fitness Area | 0.72 | 4 | Yes | No | Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage
[5 empty] | x | Storage - Hospital | 0.9 |  | Gymnasium/Fitness Center | Gymnasium - Audience Seating | Gymnasium/Fitness Center - Gymnasium - Audience Seating | S-Gymnasium/Fitness Center - Gymnasium - Audience Seating | 0.43 | 6 | Yes | No | Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage
[5 empty] | x | Storage - Museum | 0.8 |  | Gymnasium/Fitness Center | Playing Area | Gymnasium/Fitness Center - Playing Area | S-Gymnasium/Fitness Center - Playing Area | 1.2 | 4 | Yes | No | Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage
[5 empty] | x | Workshop | 1.9 |  | Hospital | Corridor/Transition | Hospital - Corridor/Transition | S-Hospital - Corridor/Transition | 0.89 | 8' wide | No | No | NA
[9 empty] | Hospital | Emergency | Hospital - Emergency | S-Hospital - Emergency | 2.26 | 6 | Yes | No | NA
[9 empty] | Hospital | Exam/Treatment | Hospital - Exam/Treatment | S-Hospital - Exam/Treatment | 1.66 | 8 | Yes | No | NA
[9 empty] | Hospital | Laundry - Washing | Hospital - Laundry - Washing | S-Hospital - Laundry - Washing | 0.6 | 4 | Yes | No | NA
[9 empty] | Hospital | Lounge/Recreation | Hospital - Lounge/Recreation | S-Hospital - Lounge/Recreation | 1.07 | 6 | Yes | No | NA
[9 empty] | Hospital | Medical Supply | Hospital - Medical Supply | S-Hospital - Medical Supply | 1.27 | 6 | Yes | No | NA
[9 empty] | Hospital | Nursery | Hospital - Nursery | S-Hospital - Nursery | 0.88 | 6 | Yes | No | NA
[9 empty] | Hospital | Nurses' Station | Hospital - Nurses' Station | S-Hospital - Nurses' Station | 0.87 | 6 | Yes | No | NA
[9 empty] | Hospital | Operating Room | Hospital - Operating Room | S-Hospital - Operating Room | 1.89 | 6 | Yes | No | NA
[9 empty] | Hospital | Patient Room | Hospital - Patient Room | S-Hospital - Patient Room | 0.62 | 6 | Yes | No | NA
[9 empty] | Hospital | Pharmacy | Hospital - Pharmacy | S-Hospital - Pharmacy | 1.14 | 6 | Yes | No | NA
[9 empty] | Hospital | Physical Therapy | Hospital - Physical Therapy | S-Hospital - Physical Therapy | 0.91 | 6 | Yes | No | NA
[9 empty] | Hospital | Radiology/Imaging | Hospital - Radiology/Imaging | S-Hospital - Radiology/Imaging | 1.32 | 6 | Yes | No | NA
[9 empty] | Hospital | Recovery | Hospital - Recovery | S-Hospital - Recovery | 1.15 | 6 | Yes | No | NA
[9 empty] | Hospital | Storage | Hospital - Storage | S-Hotel/Motel - Highway Lodging Dining | 0.88 | 4 | Yes | No | NA
[9 empty] | Hotel/Motel | Highway Lodging Dining | Hotel/Motel - Highway Lodging Dining | S-Hotel/Motel - Highway Lodging Guest Room | 0.75 | 6 | Yes | No | NA
[9 empty] | Hotel/Motel | Highway Lodging Guest Room | Hotel/Motel - Highway Lodging Guest Room | S-Hotel/Motel - Hotel Dining | 0.82 | 4 | Yes | No | NA
[9 empty] | Hotel/Motel | Hotel Dining | Hotel/Motel - Hotel Dining | S-Hotel/Motel - Hotel Guest Rooms | 1.11 | 6 | Yes | No | NA
[9 empty] | Hotel/Motel | Hotel Guest Rooms | Hotel/Motel - Hotel Guest Rooms | S-Hotel/Motel - Hotel Lobby | 1.06 | 4 | No | No | NA
[9 empty] | Hotel/Motel | Hotel Lobby | Hotel/Motel - Hotel Lobby | S-Library - Card File & Cataloging | 0.72 | 4 | Yes | No | NA | 1. Lights in corridors, electrical/mechanical rooms, public lobbies, restrooms, stairways, and storage rooms
[9 empty] | Library | Card File & Cataloging | Library - Card File & Cataloging | S-Library - Reading Area | 0.93 | 4 | Yes | No | NA | 2. Spaces with only one luminaire with rated input power less than 100 W.
[9 empty] | Library | Reading Area | Library - Reading Area | S-Library - Stacks | 1.71 | 4 | Yes | No | NA | 3. Spaces types with lighting power allowance of less than 0.6 W/sq.ft (see Table 9.6.1).
[9 empty] | Library | Stacks | Library - Stacks | S-Manufacturing - Corridor/Transition | 0.41 | 8' wide | No | No | NA
[9 empty] | Manufacturing | Corridor/Transition | Manufacturing - Corridor/Transition | S-Manufacturing - Detailed Manufacturing | 1.29 | 4 | Yes | No | NA
[9 empty] | Manufacturing | Detailed Manufacturing | Manufacturing - Detailed Manufacturing | S-Manufacturing - Equipment Room | 0.95 | 6 | Yes | No | NA
[9 empty] | Manufacturing | Equipment Room | Manufacturing - Equipment Room | S-Manufacturing - Extra High Bay (≥ 50') | 1.05 | 4 | Yes | No | NA
[9 empty] | Manufacturing | Extra High Bay (≥ 50') | Manufacturing - Extra High Bay (≥ 50') | S-Manufacturing - High Bay (≥ 25' & < 50') | 1.23 | 4 | Yes | No | NA
[9 empty] | Manufacturing | High Bay (≥ 25' & < 50') | Manufacturing - High Bay (≥ 25' & < 50') | S-Manufacturing - Low Bay (< 25') | 1.19 | 4 | Yes | No | NA
[9 empty] | Manufacturing | Low Bay (< 25') | Manufacturing - Low Bay (< 25') | S-Museum - General Exhibition | 1.05 | 6 | Yes | No | NA
[9 empty] | Museum | General Exhibition | Museum - General Exhibition | S-Museum - Restoration | 1.02 | 6 | Yes | No | NA
[9 empty] | Museum | Restoration | Museum - Restoration | S-Parking Garage - Garage Area | 0.19 | 4 | Yes | No | Lobby, Atrium, Dining Area, Corridors, Stairways, Gym, Pool, Mall Concourse, Parking Garage
[9 empty] | Museum | Storage | Museum - Storage | S-Post Office - Sorting Area | 0.94 | 4 | Yes | No | NA
[9 empty] | Parking Garage | Garage Area | Parking Garage - Garage Area | S-Religious Buildings - Audience Seating | 1.53 | 4 | Yes | No | NA
[9 empty] | Post Office | Sorting Area | Post Office - Sorting Area | S-Religious Buildings - Fellowship Hall | 0.64 | 4 | Yes | No | NA
[9 empty] | Religious Buildings | Audience Seating | Religious Buildings - Audience Seating | S-Religious Buildings - Worship Pulpit, Choir | 1.53 | 4 | Yes | No | NA
[9 empty] | Religious Buildings | Fellowship Hall | Religious Buildings - Fellowship Hall | S-Retail - Dressing/Fitting Room | 0.87 | 8 | Yes | Yes | NA
[9 empty] | Religious Buildings | Worship Pulpit, Choir | Religious Buildings - Worship Pulpit, Choir | S-Retail - Mall Concourse | 1.1 | 4 | No | No | NA
[9 empty] | Retail | Dressing/Fitting Room | Retail - Dressing/Fitting Room | S-Retail - Sales Area | 1.68 | 6 | Yes | No | Retail Sales Area
[9 empty] | Retail | Mall Concourse | Retail - Mall Concourse | S-Sports Arena - Audience Seating | 0.43 | 4 | Yes | No | NA
[9 empty] | Retail | Sales Area | Retail - Sales Area | S-Sports Arena - Court Sports Area - Class 1 | 3.01 | 4 | Yes | No | NA
[9 empty] | Sports Arena | Audience Seating | Sports Arena - Audience Seating | S-Sports Arena - Court Sports Area - Class 2 | 1.92 | 4 | Yes | No | NA
[9 empty] | Sports Arena | Court Sports Area - Class 1 | Sports Arena - Court Sports Area - Class 1 | S-Sports Arena - Court Sports Area - Class 3 | 1.2 | 4 | Yes | No | NA
[9 empty] | Sports Arena | Court Sports Area - Class 2 | Sports Arena - Court Sports Area - Class 2 | S-Sports Arena - Court Sports Area - Class 4 | 0.72 | 4 | Yes | No | NA
[9 empty] | Sports Arena | Court Sports Area - Class 3 | Sports Arena - Court Sports Area - Class 3 | S-Sports Arena - Ring Sports Area | 2.68 | 4 | Yes | No | NA
[9 empty] | Sports Arena | Court Sports Area - Class 4 | Sports Arena - Court Sports Area - Class 4 | S-Transportation - Air/Train/Bus Baggage Area | 0.76 | 4 | Yes | No | NA
[9 empty] | Sports Arena | Ring Sports Area | Sports Arena - Ring Sports Area | S-Transportation - Airport Concourse | 0.36 | 4 | No | No | NA
[9 empty] | Transportation | Air/Train/Bus Baggage Area | Transportation - Air/Train/Bus Baggage Area | S-Transportation - Audience Seating | 0.54 | 4 | Yes | No | NA
[9 empty] | Transportation | Airport Concourse | Transportation - Airport Concourse | S-Transportation - Terminal - Ticket Counter | 1.08 | 4 | Yes | No | NA
[9 empty] | Transportation | Audience Seating | Transportation - Audience Seating | S-Warehouse - Fine Material Storage | 0.95 | 6 | Yes | No | NA
[9 empty] | Transportation | Terminal - Ticket Counter | Transportation - Terminal - Ticket Counter | S-Warehouse - Medium/Bulky Material Storage | 0.58 | 4 | Yes | No | NA
[9 empty] | Warehouse | Fine Material Storage | Warehouse - Fine Material Storage
[9 empty] | Warehouse | Medium/Bulky Material Storage | Warehouse - Medium/Bulky Material Storage

## 9.4.1.1 (16)
2016 - 9.4.1.1 Interior Lighting Controls
9.4.1 Lighting Control
Building lighting controls shall be installed to meet the provisions of Sections 9.4.1.1, 9.4.1.2, 9.4.1.3 and 9.4.1.4.
9.4.1.1 Interior Lighting Controls
For each space in the building, all of the lighting control functions indicated in Table 9.6.1, for the appropriate space type in the first column, and as described below, shall be implemented. All control functions indicated as “REQ” are mandatory and shall be implemented. If a space type has control functions indicated as “ADD1,” then at least one of those functions shall be implemented. If a space type has control functions indicated as “ADD2,” then at least one of those functions shall be implemented. For space types not listed, select a reasonably equivalent type.
If using the Space-by-Space Method, the space type used for determining control requirements shall be the same space type that is used for determining the LPD allowance.
a. Local control: There shall be one or more manual lighting controls in the space that controls all of the lighting in the space.
Each control device shall control an area (1) no larger than 2500 ft2 if the space is £10,000 ft2 and (2) no larger than 10,000 ft2 otherwise. The device installed to comply with this provision shall be readily accessible and located so that the occupants can see the controlled lighting when using the control device.
Exception to 9.4.1.1(a)
Remote location of this local control device or devices shall be permitted for reasons of safety or security when each remote control device has an indicator pilot light as part of or next to the control device and the light is clearly labeled to identify the controlled lighting.
b. Restricted to manual on: None of the lighting shall be automatically turned on.
Exception to 9.4.1.1(b)
Manual on is not required where manual on operation of the general lighting would endanger the safety or security of the room or building occupants.
c. Restricted to partial automatic on: No more than 50% of the lighting power for the general lighting shall be allowed to be automatically turned on, and none of the remaining lighting shall be automatically turned on.
Exception to 9.4.1.1(c)
Lighting in open-plan office spaces shall be allowed to turn on automatically to more than 50%, provided the control zone is no larger than 600 ft2.
d. Bilevel lighting control: The general lighting in the space shall be controlled so as to provide at least one intermediate step in lighting power or continuous dimming in addition to full on and full off. At least one intermediate step shall be between 30% and 70% (inclusive) of full lighting power.
e. Automatic daylight responsive controls for sidelighting: In any space where the combined input power of all general lighting completely or partially within the primary sidelighted areas is 150 W or greater, the general lighting in the primary sidelighted areas shall be controlled by photocontrols.
In any space where the combined input power of all general lighting completely or partially within the primary sidelighted area and secondary sidelighted area is 300 W or greater, the general lighting in the primary sidelighted area and secondary sidelighted area shall be controlled by photocontrols. General lighting in the secondary sidelighted area shall be controlled independently of the general lighting in the primary sidelighted area.
The control system shall have the following characteristics:
1. The calibration adjustment control shall be located no higher than 11 ft above the finished floor.
2. The photocontrol shall reduce electric lighting in response to available daylight using continuous dimming or with at least one control point between 50% and 70% of design lighting power, a second control point between 20% and 40% of design lighting power or the lowest dimming level the technology allows, and a third control point that turns off all the controlled lighting.
3. The calibration shall not require the physical presence of a person at the sensor while the calibration is processing.
Exception to 9.4.1.1(e)
The following areas are exempted from Section 9.4.1.1(e):
1. Primary sidelighted areas where the top of any existing adjacent structure is twice as high above the windows as its distance away from the windows.
2. Sidelighted areas where the total glazing area is less than 20 ft2.
3. Retail spaces.
f. Automatic daylight responsive controls for toplighting: In any space where the combined input power for all general lighting completely or partially within daylight area under skylights and daylight area under roof monitors is 150 W or greater, general lighting in the daylight area shall be controlled by photocontrols. The control system shall have the following characteristics:
1. The photocontrol shall reduce electric lighting in response to available daylight using continuous dimming or with at least one control point that is between 50% and 70% of design lighting power, a second control point between 20% and 40% of design lighting power or the lowest dimming level the technology allows, and a third control point that turns off all the controlled lighting.
2. The calibration shall not require the physical presence of a person at the sensor while the calibration is processing.
3. General lighting in overlapping toplighted and sidelighted daylight areas shall be controlled together with general lighting in the daylight area under skylights or daylight area under roof monitors.
Exception to 9.4.1.1(f)
The following areas are exempted from Section 9.4.1.1(f):
1. Daylight area under skylights where it is documented that existing adjacent structures or natural objects block direct sunlight for more than 1500 daytime hours per year between 8 a.m. and 4 p.m.
2. Daylight area under skylights where the overall skylight effective aperture for the enclosed space is less than 0.006.
3. In each space within buildings in Climate Zone 8 where the input power of the general lighting within daylight areas is less than 200 W.
g. Automatic partial off (full off complies): The general lighting power in the space shall be automatically reduced by at least 50% within 20 minutes of all occupants leaving the space.
Exception to 9.4.1.1(g)
This requirement does not have to be complied with in spaces that meet all three of the following requirements:
1. The space has an installed LPD of no more than 0.80 W/ft2.
2. The space is lighted by HID lamp.
3. The general lighting power in the space is automatically reduced by at least 30% within 20 minutes of all occupants leaving the space.
4. Lighting load does not exceed 0.02 W/ft2 multiplied by the gross lighted floor area of the building.
h. Automatic full off: All lighting, including lighting connected to emergency circuits, shall be automatically shut off within 20 minutes of all occupants leaving the space. A control device meeting this requirement shall control no more than 5000 ft2.
Exception to 9.4.1.1(h)
The following lighting is not required to be automatically shut off:
1. General lighting and task lighting in shop and laboratory classrooms.
2. General lighting and task lighting in spaces where automatic shutoff would endanger the safety or security of room or building occupants.
3. Lighting required for 24/7 operation.
4. Lighting load not exceeding 0.02 W/ft2 (.22 W/m2) multiplied by the gross lighted area of the building.
i. Scheduled shutoff: All lighting in the space, including lighting connected to emergency circuits, shall be automatically shut off during periods when the space is scheduled to be unoccupied using either (1) a time-of-day operated control device that automatically turns the lighting off at specific programmed times or (2) a signal from another automatic control device or alarm/security system. The control device or system shall provide independent control sequences that (1) control the lighting for an area of no more than 25,000 ft2, (2) include no more than one floor, and (3) shall be programmed to account for weekends and holidays. Any manual control installed to provide override of the scheduled shutoff control shall not turn the lighting on for more than two hours per activation during scheduled off periods and shall not control more than 5000 ft2.
Exception to 9.4.1.1(i)
The following lighting is not required to be on scheduled shutoff:
1. Lighting in spaces where lighting is required for 24/7 continuous operation.
2. Lighting in spaces where patient care is rendered.
3. Lighting in spaces where automatic shutoff would endanger the safety or security of the room or building occupants.
4. Lighting load not exceeding 0.02 W/ft2 multiplied by the gross lighted floor area of the building.
Return to Top of Compliance Worksheet
Return to General
Control Requirement
Return to
Building Area
9.4.1a
Return to Retail
Control Requirement
Return to
Building Area
9.4.1b
Return to
Building Area
9.4.1c
Return to
Building Area
9.4.1d
Return to
Building Area
9.4.1e
Return to
Building Area
9.4.1f
Return to
Building Area
9.4.1h
Return to
Building Area
9.4.1i
Return to
Space-by-Space 9.4.1a
Return to
Space-by-Space 9.4.1b
Return to
Space-by-Space 9.4.1c
Return to
Space-by-Space 9.4.1d
Return to
Space-by-Space 9.4.1e
Return to
Space-by-Space
9.4.1f
Return to
Building Area
9.4.1g
Return to
Space-by-Space
9.4.1g
Return to
Space-by-Space
9.4.1h
Return to
Space-by-Space
9.4.1i

## 9.4.1.2 (16)
2016 - 9.4.1.2 Parking Garage Lighting Controls
Lighting for parking garages shall comply with the following requirements:
a. Parking garage lighting shall have automatic lighting shutoff per Section 9.4.1.1(i).
b. Lighting power of each luminaire shall be automatically reduced by a minimum of 30% when there is no activity detected within a lighting zone for 20 minutes. Lighting zones for this requirement shall be no larger than 3600 ft2.
c. Lighting for covered vehicle entrances and exits from buildings and parking structures shall be separately controlled by a device that automatically reduces the lighting by at least 50% from sunset to sunrise.
d. The power to luminaires within 20 ft of any perimeter wall structure that has a net opening-to-wall ratio of at least 40% and no exterior obstructions within 20 ft, shall be automatically reduced in response to daylight by at least 50%.
Exception to 9.4.1.2(d)
Lighting in the following areas is exempt:
1. Lighting in daylight transitions zones and ramps without parking.
Return to Top of Compliance Worksheet
Return to
Building Area
Parking Garage Control
Return to
Space-by-Space
Parking Garage Control